Special report on Session 2 :   POWER QUALITY & EMC

A. Robert (Chairman), E. De Jaeger and J. Hoeffelman (Rapporteurs), Belgium

###### Contents

Introduction – Call for Contributions	1

I	EMI, EMF and Safety	1

Electromagnetic Interferences (EMI)	2

Lightning	2

Ground Potential Rise and neutral grounding	3

Electromagnetic fields	3

II	Connection of disturbing installations	4

Harmonics and distorting loads	4

Harmonics and flicker: industrial case studies and mitigation techniques	6

Power Quality measurement methods	7

III	Voltage dips and disturbances in customers installations	8

Measurement and characterization of voltage dips and short interruptions	8

Immunization techniques	10

Techno-economical assessment	11

Voltage dip related industrial power quality problems	12

IV	Power Quality in the competitive market	12

Context	12

Benchmarking utilities	13

Obtaining and analysing reliability data	14

Power Quality monitoring	16

Customer relationships	17

Power Quality related Papers in other Sessions	19

List of Papers	21

# Introduction – Call for Contributions

The scope of Session 2 has been defined as follows by the Session Advisory Group :

(	Power Quality, i.e. voltage continuity (often referred to as supply reliability - problem of outages) and voltage quality (LF disturbances, ( 9 kHz, reaching equipment through the electricity supply) ;

(	EMI, EMF and Safety :  HF disturbances on the electricity supply and all disturbances - HF or LF - reaching equipment other than through the electricity supply ; some safety and resistibility concerns (Electromagnetic fields - overvoltages - step, touch and transferred voltages...) are also considered.

N.B.  The concept of Quality of Supply is a little broader than Power Quality. In addition to Voltage Continuity and Voltage Quality, it includes the Commercial Quality (quality of response to telephone calls, etc.).

The 2003 session will be divided in four blocks of 90 minutes: 1)  EMI, EMF, Safety,

2)  Connection of disturbing installations (emission limits for harmonics, flicker or unbalance ; filters or compensators, etc.) and monitoring methods,

3)  Voltage dips and disturbances in customers installations (immunity levels, remedial measures, etc),

4)  Power quality as seen by the different players in the competitive market (system operator, regulator, customers, etc).

Each block will be divided in two main parts :

1)  a few presentations by key note speakers or authors,

2)  discussion (prepared contributions and free discussion).

The aim of this special report is :

1)  to present a synthesis of the present concerns in each of the four sections, mainly based on the selected papers,

2)  to call for prepared contributions on particular points which appear in the papers or which are not covered by them,

3)  to stimulate the free discussion.

Call for prepared contributions. Prepared contributions will preferably aim at answering the questions of the Special Report. However, other kinds of contributions will be welcome :

-	fresh information on particular points which appear in the papers or which are not covered by them ;

-	case studies (outstanding disturbance experiences, causes, solutions...) ;

-	comments on a particular paper (“I agree/disagree with that result/conclusion”, "My own practical experience in the same field is...") ;

-	just plain questions to the author of a paper.

According to the successful experiment since CIRED 1997, all prepared contributions will be made available to attendees at the entrance of the conference room. Furthermore, some of the most relevant ones will be selected for a verbal presentation (second part of each section).

# General guidelines for authors of prepared contributions :

-	language: preferably English for the written document ;

-	starting with: title, name of author(s), affiliation, country, number of the relevant question in the special report or number of the commented paper ;

-	font: Arial or Times New Roman, size: 10, margins: 2.5 cm top and bottom, 1.8 cm left and right, preferably two columns with 0.5 cm gap ;

-	maximum length: 2 pages, including both text and illustrations (this allows for a lot of information if a 2-column presentation is chosen) ;

-	if you wish to use a Power Point slide show, please send the Power Point file also (only ppt files received in advance will be available in the computer on the platform) ;

-	deadline : 29 April 2003 (possibly 5 May at the very latest) ;

- addresses : alain.robert@elia.be ; jean.hoeffelman@elia.be ; emmanuel.dejaeger@laborelec.be ; info@cired2003.be.

# I	EMI, EMF and Safety

Four different topics will be addressed in this first part of the session: Pure EMI subjects dealing with immunity and emission, lightning related questions, Ground Potential Rises (GPR) and neutral grounding practices with their influence on power quality and on safety and, finally, EMF (Electromagnetic fields).

## Electromagnetic Interferences (EMI)

As already stated during the previous sessions, pure EMI problems (i.e. interferences between equipment or systems) are not very often discussed in CIRED, probably because they are considered as too specific and left to more specialised forums.

Four papers, however, address directly EMI questions. The first, paper 2.4 (JP), highlights experimentally the well-known problem of common impedance coupling (under lightning surge conditions) on the auxiliary cabling of HV substations. Also related to HV substations, paper 2.13 (ES) presents a detailed analysis of the disturbances produced by switching of disconnectors. Many papers have already been published on that question, mainly in CIGRE and IEEE, but the link with the standardised assessment methods and the need to improve them is seldom highlighted. The influence of power lines on long structures like pipelines and telecommunication lines cables is often analysed in CIRED and CIGRE papers but less frequently the inductive coupling of power cables on nearby telecommunication links. This problem is discussed in paper 2.18 (CN) with a special attention on the cable screen grounding.

A completely different and quite new topic is introduced in paper 2.11 (ES) dealing with broadband power line carrier (PLC). Emission problems related to PLC will probably become more stringent in the future if this new technology really succeeds in challenging the other classical telecommunication media (like ADSL).

Question 1

  - Common impedance coupling is the price to pay when single point and independent grounding practices are abandoned in favour of meshed structures and equipotential bonding. It is important to highlight these risks but are there reasons to believe that the general cabling practices presented in CIGRE guide 124 and in IEC guide 61000-6-5 should be amended accordingly?

  - The need to improve the IEC 61000-4-12 transient oscillatory wave test (and the related 60255-22-1 standard) has been admitted by IEC. This basic standard, however, is seldom used outside the power industry. Therefore, is there a sufficient marked need to justify the revision of this standard? In absence of this revision can the IEC 61000-4-4 fast transient test be considered as equivalent ?

  - It is well known that coupling between power cables and telecommunication cables is highly reduced when the cable screens are earthed at both ends and when cross bonding is applied. In what cases could this good EMC (and safety) practice not be applied? Are there other related experiences?

  - As stated in paper 2.11 broadband PLC will probably take an increasing market place in the future. Is it correct to state that EMC is one of the most important problems this new technology has to face? Has an international agreement on the emission limits finally been reached?

## Lightning

Lightning overvoltages (OV) and lightning protection remain one of the most important concerns system operators have to face. Indeed, not less than 8 papers presented at this session address this topic:

Paper 2.23 (ES) presents a warning system based on the use of an electric “field mill”. Paper 2.1 (BR) develops a model for the statistical analysis of the OV and the necessary related insulation coordination. Starting from a case study, paper 2.2 (ES) analyses the interruptions due to lightning and the OV protection of a mixed cable-overhead network. Another case study related to the protection of a small hydroelectric plant connected to a network with isolated neutral is proposed in paper 2.7 (ES). A more systematic approach based on Monte Carlo simulations and on the use of fuzzy logic techniques is applied in paper 2.22 (ES) for the protection scheme of mixed networks. The special case of the protection of covered conductors is addressed in paper 2.19 (RU) which makes recourse to an original antenna-type arrester, whereas paper 2.20 (NL-MK) dealing with radio base stations on HV towers makes the link with power frequency ground potential rise problems and with transfer of potentials from HV to LV networks. This latter report shows clearly the difference in behaviour of grounding systems depending on the frequency spectrum involved (cf. figure 1)

Figure 1:  Current distribution between earth wires, tower grounding and metal shields of MV/LV cable

for ( = 100 (m

Question 2

- When can it be recommended to link the automatic disconnection of an installation to the use of a lightning warning system?

- What are the advantages and drawbacks of using covered conductors with respect to classical overhead lines? Is this technique sometimes used to reduce EMF? Up to what rated voltage can it be applied?

- Many formulas have been published concerning the statistics of direct and indirect lightning OV (cf paper 2.1 and 2.2). Are these formulas in good agreement with the modern computation techniques and with the measurement data?

- The calculation of the best location for surge arresters needs not only powerful tools but also the input of all the characteristics of the analysed network. How far can such tools be applied for practical cases? Are codes like Matlab, with all their modules, becoming more powerful than dedicated programs like EMTP? Isn’t it possible to draw, from a set of simulations, some practical guidelines?

- Most protection schemes are based on good insulation coordination and the use of well located MO arresters. However, particularly when the soil resistivity is high, shouldn’t it be useful to pay more attention to the equipotential bonding ?

- The protection of radio base station installed on HV tower has led to a close collaboration between Cigre, Cired and UIT-T and, hence, to a draft Kbsp recommendation. Do the conclusions of paper 2.20 modify the protection scheme proposed by UIT-T ? What are the practical consequences of the use of LV cables without metal sheat ?

## Ground Potential Rise and neutral grounding

Ground potential rises (GPR) can be produced by lightning or by fault current. In the first case they lead mainly to insulation coordination problems and therefore have been addressed together with the other lightning related problems. In the second case they lead to temporary overvoltages (TOV) and, depending on the neutral distribution scheme, to possible step and touch voltages. GPR problems are also tightly linked to the way the neutral is grounded, to the protection scheme used and finally to the power quality.

Seven papers address these topics:

Paper 2.10 (CA) and 2.21 (NL) propose, for low resistance or direct grounding networks, in situ assessment procedures based on the injection of currents at frequencies slightly different from the power frequency. Paper 2.10 highlights also the differences that exist between a rural network and a urban network, this latter taking benefit of the global earthing (cf. figure 2). Paper 2.14 (CH) focuses on the risk of resonance induced overvoltages in 110 kV networks grounded through reactors. Paper 2.3 (DK) points out the facts that harmonics are not compensated in MV networks grounded through an arc suppression coil (Petersen) and, hence, could produce voltages exceeding the allowed limits. Paper 2.17 (DE) gives a interesting analysis of the possible solutions to improve the quality of supply of an industrial MV network by letting the neutral grounding evolve from insulated to low resistance. Alternatively, paper 2.5 (ES) shows how the evolution from a solidly grounded network to a resonant grounded system can be a good solution in a mixed network. Paper 2.16 (DE), on the other hand, proposes an original way to adopt different neutral grounding schemes in the different parts of a network depending of the proportion of overhead lines involved.

Figure 2 :  Touch voltages in LV installations during a 
phase-to-neutral fault on overhead MV lines

Question 3

- Standards like HD 637 S1 or IEC 61936 propose safety limits for touch voltages in HV installations. These limits are generally higher than the limits adopted in the different countries for LV installations. Although, as stated in paper 2.10, no accident in LV installations due to faults in HV installations seems to have ever been reported, are there countries where, in case of propagation of potential, the HV safety limits have been accepted in LV installations? If not what are the common practices?

- Low impedance limitation of zero sequence current seems to be one of the best practices for (underground) MV networks. What are, in that respect, the pro and contra of reactors versus resistors? Up to which rated voltage is it safe to apply this type of neutral grounding? How far could the conclusions of paper 2.17 (to limit at 500 A instead of 2000 A) be transposed to a public distribution network?

- On basis of the papers presented, two different trends seem to coexist in MV networks: Evolution towards resonant grounding or evolution towards low impedance grounding. What are, besides the ratio underground/overhead and the weight of the past, the main rationales for choosing one or the other grounding scheme?

## Electromagnetic fields

Severe regulation or (uncontrolled) recourse to the precautionary principle often lead to the application of mitigation techniques in order to reduce EMF in the vicinity of power installations. Switzerland (see figure 3) and Slovenia are two countries where much more severe limits than those recommended by ICNIRP are legally applied. Paper 6 (SI) shows even that very restrictive limits on the E field can oblige the utilities to take more care of this latter than of the magnetic field ! Paper 8 (CH) shows, on the other hand, that the costs involved for ensuring the compliance with the regulation could be much higher for existing installations than for new ones. Dealing with the assessment of installations, paper 15 (FR) points out the difficulties related to the share of responsibilities between manufacturer and contractor, to the influence of the cabling and to the definition of the rated conditions. A completely different sound is found in paper 2.12 (ES) that highlights the rationales of a judgement stating that exposure to EMF of less than 100 µT has no adverse effects on public health !

Figure 3 :  Installation Limit Values and Exposure Limit Values according to the Swiss regulation. The dashed line means a minimum measuring distance of 0.2 m

Question 4

- Authorities too often set limits without specifying the way to assess the compliance of installations. Are the limits for “rated” conditions or “normal” conditions? (But what is the meaning of “rated” or “normal” conditions?) Are they simply maximum values or values not exceeded during a given percentage of the time? Is there a minimum distance to the source like that suggested in paper 2.8 (but apparently not present in the Ordinance)?

- The Swiss Ordinance seems to open a door and to allow derogations when the owner of the installation can prove that he has taken appropriate (and economically affordable) mitigation measures. How far is this of application? In the framework of the EU, the legality of Swiss regulation could probably be fought because it applies some discrimination (e.g. the limits are not the same for railways installations as for power installations). Are there other known examples of discriminating regulation?

- Paper 2.8 mentions costs as high as € 35 000 for ensuring the compliance of existing MV/LV substations. Are there other evaluations available?

- An important judgement in Spain seems to be considered as a legal “precedent”. What are the similar experiences in other countries? Could the fact that WHO and IARC statements are not taken as reference in the Spanish judgement be considered as a weakness for the jurisprudence?

# II	Connection of disturbing installations

(emission limits for harmonics, flicker or unbalance; filters or compensators)

## Harmonics and distorting loads

Among LF disturbing phenomena, harmonics are still receiving much attention from energy service companies and grid operators. Harmonics are basically produced by distorting loads (non linear loads) that may be found everywhere, at all voltage levels, from LV distribution (household appliances using switching mode power supply such as TV sets, personal computers, compact fluorescent lamps etc) to MV or HV levels, where big industrial consumers or dispersed generation units are connected (power electronics interfaces, adjustable speed drives, welding machines, arc or induction furnaces and so forth).

The work reported about harmonics in this session covers:

- Large scale measurement campaigns in distribution or transmission networks,

- Case studies of connection of distorting loads, including the difficult problem of the assessment of individual emission levels,

- Solutions to industrial harmonics problems and mitigation techniques (active filters).

Paper 2.31 (FR) discusses the major conclusions from a harmonic survey on French LV networks since 2000.

E.g. 5th harmonic voltages, in 2001, on a sample of 16 typical LV networks (Figure 4):

  - the 95% level measured over one year was between 4 and 6% for more than 60% of the networks;

  - about 20% of the networks did not comply with standard EN 50160.

Figure 4 :  5th harmonic yearly measurement results 
(sample of 16 typical French LV networks in 2001)

In order to observe the time evolution, EDF will continue the harmonic survey on the same sample of typical LV networks for several years. According to the authors, if the increase of harmonic levels is confirmed, the situation on the French distribution networks will be critical in the medium term. In this case, more efficient solutions will have to be applied, and, in particular, more severe emission limits for equipment and installations.

Additional measurements on typical LV networks in 2002 showed important harmonic voltage differences for the 3rd and 9th harmonic voltages along the feeders (Figure 5). For these harmonic orders, although the levels are generally low in MV/LV substations, the compatibility levels may be exceeded at the end of typical LV feeders (the same conclusion is also pointed out in Paper 2.38 (BE)).

Figure 5: time evolution of the 3rd harmonic voltage 
over one week: 10-minute average values

Paper 2.77 (NL) summarizes the findings of harmonics monitoring programs conducted by NUON in the Netherlands during the second half of the nineties, at various voltage levels.

No significant increase in harmonics can be discerned from 6 years of measurement.

According to the authors, harmonic problems are not due to excessive emission but rather the consequence of resonance. Local harmonic problems are usually caused by a parallel resonance for a specific frequency while Power Quality problems over a large area are the consequence of series resonance.

Taking into account the loads, generations, grid configuration and operation of reactive power compensation, the realistic prediction of resonance in the grid seems to be quite a challenge for the future.

The massive penetration of electronically controlled devices and equipment in low voltage distribution networks (the "digital society") could be responsible for the worsening of power quality problems.

Combinations of such loads may result in serious non-symmetrical loading of distribution networks, with overloading of the neutral conductor and increase of the losses. The authors of Paper 2.34 (RO) propose an approach to correctly incorporate in a mathematical model, the impact of the most significant disturbances, i.e. non-symmetrical loading combined with non-sinusoidal operating regime. Quantitative assessments are given.

Harmonics propagation mechanisms in distribution networks and influencing factors are thoroughly investigated in Paper 2.38 (BE). Differences in distribution system design and simulation approach are studied. Among the conclusions, it appears that single-phase conductors reduce the voltage THD at the load node near the end of the feeder.

New families of power electronics converters, using pulse width modulation (PWM), are more and more widely used today. One of the most growing applications is the connection of non-conventional power generators to MV or even LV distribution grids (variable speed windmills, micro-turbines, photovoltaic generators etc.).

Two reports investigate the harmonic disturbances produced by such devices (Papers 2.36 (FR) and 2.40 (DE)).

Due to their working principle, PWM converters are well known to produce frequency components in the range of several kHz (typically between 2 to 16 kHz). Paper 2.36 (FR) shows that a quick evaluation of these components is possible, taking the main influencing parameters into account. Measurements were also carried out (see e.g.

Figure 6) showing a good agreement with predictions.

Figure 6: Example of measured current components 
in the range 2 to 9 kHz (the characteristic components 
appear to have frequencies surrounding multiples 
of the switching frequency of the converter)

Paper 2.40 (DE) describes another approach to modelling power electronic devices and power distribution networks in the frequency domain, using frequency-coupling matrices. An example is treated with two back-to-back PWM converters feeding a simple L/R load.

It is shown, that the characteristic and non-characteristic harmonics and interharmonics result from three main mechanisms:

- Harmonics generated by the switching of one converter only, resulting in characteristic harmonics. These harmonics may have significant amplitudes, depending on the modulation index.

- Non-characteristic harmonics and interharmonics generated by one converter as a result of the switching of the second converter. This mechanism leads to non-characteristic harmonics if both converters operate at the same switching frequency and to interharmonics if they operate at different switching frequencies. This leads to distortions with generally small amplitudes.

- Non-characteristic harmonics and interharmonics due to AC side impedance unbalance. Depending on the degree of unbalance this mechanism leads to distortions that may have significant amplitudes.

Besides controlling the emission limits, as suggested in Paper 2.31, some technical solutions could be investigated to mitigate the effects of harmonics in a centralized manner. Paper 2.33 (DE) is describing a new method to determine the optimal placement and the mutual static and dynamic interaction of active filters for harmonics in power systems. It provides an easy way to derive statements about the mutual influence of two or more active filters or compensators from general network parameters. Using the original distortion levels and the power system’s impedance matrix, an analytical solution for optimal placement of active filters can be calculated.

The assessment of harmonic emission level from a particular distorting load is dealt with in Papers 2.32 (FR) and 2.37 (RU).

Harmonic current flowing at an installation’s metering point results from harmonics originating in this installation and also in other installations connected to the same power system.

The basic idea developed in Paper 2.32 (FR) is to scrutinize sudden harmonic variations at the point of common coupling using the sign of . An iterative method makes it possible to follow the estimates of harmonic impedances and currents over the time. A non-linear regression method is used to complete the assessment for periods with no significant harmonic variation,.

The authors trust that the method will gain sufficient precision in the medium term to allow for its use within a contractual framework application.

Paper 2.37 (RU) presents the application of a similar method for estimating the influence of voltage distortion sources at the border between two subsystems.

The method is based on the results of continuous long duration measurements (more than 24 hours) from which the correlation factor between the controlled harmonic and the load of the subsystem is estimated, as well as the distortion power sign. According to this criterion the so-called dominant subsystem is determined.

Measurements performed in an actual power supply system confirm the practical usefulness of the suggested method (see the example given in

Figure 7)

Figure 7:  Example of the determined respective impacts of 
the power supply system and a particular consumer load (trolleybus traction substation) in 13-th harmonic voltage

Question 5

5.1	Is there a general trend towards the increase of harmonics levels in distribution networks?

5.2	Are there practical measurement experiences of the harmonic emission level from a particular distorting industrial consumer or load? How is this problem usually dealt with, from a practical point of view, for contractual purposes?

5.3	Are there any practical experiences of applying the IEC recommendations for the assessment of harmonic emission limits for big distorting loads at LV level (IEC 61000-3-4 and IEC 61000-3-12)? What are the major difficulties linked to their application? Are other methods or approaches considered?

5.4	Is the central harmonic compensation with active filters already used? Is there actually a need to do this? Are there projects towards this solution? What are the major advantages and drawbacks?

5.5	Are there any practical experiences involving the disturbances generated by PWM converters in the range 2 to 16 kHz? What are the EMC problems to be feared with such components?

5.6	Besides harmonics, are there any recent experiences or interesting cases-studies with other distorting-type disturbances (e.g. interharmonics, transients)?

## Harmonics and flicker: industrial case studies and mitigation techniques

Paper 2.24 (SE) explains how the London underground is connected to the public grid in order to limit the disturbances. A total of five Static Var Compensators (SVC) and ten harmonic filters have been installed in critical points of the LUL 22 kV distribution grid. Due to the scarceness of space and vicinity to underground stations, special measures had to be taken to lay out the hardware in a compact way as well as ensure adequate confinement of noise and magnetic fields.

Another interesting industrial application is described in Paper 2.30 (CH). A new SVC was designed and installed for CERN’s Super Proton Synchrotron (SPS) accelerator. Due to the sensitive nature of the converter of the SPS magnets, very strict requirements were imposed on the stabilization of the 18 kV bus voltage and its harmonic distortion. The adopted solution comprises a 150 Mvar TCR and eight harmonic filters with a total power of 130 Mvar.

Problems frequently encountered with capacitor banks in industrial premises are listed in Paper 2.35 (ES).

While actual problems in MV utilities are related to capacitor switching, and less frequently to harmonics or other PQ issues, a very complete list of problems can be found within industrial sites. Harmonic resonance is currently appearing, as expected, but also damages due to high order harmonics or interharmonics, or due to high frequency overvoltages and even EMC problems.

In contrast to utilities, the nominal power of capacitor banks in some industries can be higher than the transformer power. Some loads consume more reactive power than active power. Various factors affect the harmonic contents or give rise to addition laws different from those generally used in distribution networks (closer to arithmetic summation in industries).

Mostly the owner of the capacitor bank suffers himself the effects of disturbances. Nevertheless, capacitor banks directly connected at the Point of Common Coupling (PCC) are cases that must be considered carefully. Harmonics can affect the whole MV system, especially when there are changes in the network impedance. Another problem of this configuration is the unexpected presence of high frequency currents that can cause damages to the breaker of the utility’s capacitor bank.

The problem of compensating electric arc furnaces flicker is addressed in Paper 2.28 (UK). This paper develops a transient model for 11-level cascade converters-based STATCOM. A proposed new control strategy has the benefits of faster response and more accuracy.

Paper 2.41 (DE) investigates the disturbances emanated from welding devices. An experimental approach, based on a measurement method involving synchronous measurements both at the device’s clamps and at the substation bus, is described (Figure 8). A mathematical model is presented and discussed.

Figure 8:  Welding device - Harmonic content of the voltage measured at the clamps and at the distribution substation

Figure 8 shows that the 3rd harmonic damping along the cable is nearly constant over the whole power range, while the 5th damping varies. This is because of the interaction between the 5th harmonic component present in the supply voltage and the component introduced by the welder.

It is interesting to see that the maximum distortion injected by this machine into the supply voltage lies near the point of 40-50% nominal power and consists mainly of the 3rd harmonic. Its propagation is blocked by the delta-star step–down transformers. However, careful attention should be paid to the neutral cable, which can be overloaded in the case of multiple devices.

Question 6

6.1	What are the most remarkable harmful effects of harmonics (and interharmonics) as encountered in industrial practice? Are they different in public distribution networks? What are the most frequently used mitigation devices or techniques?

6.2	Are there any other interesting industrial experiences with modern flicker compensating devices such as the SVC or the STATCOM?

6.3	Are there any experiences in LV (such as e.g. the compensation of welding devices)?

## Power Quality measurement methods

Paper 2.25 (PL) reports on comparative tests of flickermeters designed according to the requirements of IEC 61000-4-15 standard. Measurements were carried out at one Polish steelwork (seven days). Ten various IEC 61000-4-15 compliant flickermeters have been used for these measurements. These measurements and further laboratory tests showed that the standard requirements are not enough precisely formulated, leaving designers too much freedom.

Paper 2.29 (ES) presents a system for real time identification of different types of power quality disturbances in power systems (voltage dips, short interruptions and transient or temporary overvoltages). The proposed method estimates the magnitude of the three-phase voltage supply in real time in order to determine when a voltage event appears, making use of three Kalman filters.

Using this method, the start of a voltage event can be detected accurately with detection times ranging from less than 1 millisecond to about 8 milliseconds, depending on the magnitude of the voltage event and the point on the wave when it starts.

Question 7

7.1	Is the recently published IEC standard 61000-4-30 (Power Quality measurement methods) well known? Are there already measuring devices, compliant with this standard? Are there any difficulties to implement the methods described in the standard?

7.2	What are the difficulties related to the measurement transducers (voltage and current transformers)? Up to which frequency is it practically realistic to perform accurate measurements?

7.3	What are the new trends in Power Quality assessment methods? Are there any recent experiences using advanced techniques such as wavelet analysis or similar?

# III	Voltage dips and disturbances in customers installations

(immunity levels, remedial measures, etc)

Solving power quality problems within industrial consumers premises is a rather complex task involving, generally speaking, the following steps, as discussed in Paper 2.45 (ES):

- Power Quality monitoring in order to characterize the main involved disturbances as well as the actual immunity level of the installation,

- Analyzing the sensitive processes and identifying the critical parts,

- Choosing the adequate immunization techniques

- Costs estimation: balance between the costs caused by the disturbances and the investment and costs related to the immunization project

- Decision of implementing the solution

Paper 2.58 (MY) stresses that close cooperation between the utility and the customer is mandatory for such operation to succeed since both the customer and the utility engineers will have to act as a team in the process of understanding the power system dynamic and equipment behaviour.

Power Quality in its complexity involves grid operators, energy service companies, end users, equipment manufacturers and finally manufacturers of technical solutions and measuring equipment. Electrical designers play a crucial role to make the optimum choice of different solutions (Paper 2.55 (PL)).

## Measurement and characterization of voltage dips and short interruptions

Voltage dips at the terminals of sensitive equipment are often due to faults occurring at a much higher voltage level. Even though the load current is small compared to the fault current, the changes in load current during and after the fault still strongly influence the voltage at the equipment terminals. Paper 2.47 (SE) discusses the changes in shape and magnitude of the voltage dip during its propagation from the faulted voltage level down to the equipment terminals. Both balanced and unbalanced voltage dips are discussed. Studies of voltage-dip propagation due to symmetrical and non-symmetrical faults can be simplified using the related dip characteristics - “characteristic voltage” and “PN-factor”.

The conclusions for induction-motor loads are:

- for short-duration dips the positive-sequence voltage increases from the faulted level towards the load. This increase is due to the motor-contribution to the fault and it becomes less after a few cycles.

- for long-duration dips and large amounts of motor load, the motor load will take a larger current when its speed drops, thus leading to a drop in voltage which will be larger towards the load.

- the negative-sequence voltage becomes less when moving from the fault to the load. It is constant during the fault.

From a qualitative analysis it is concluded that the behavior of other load is similar to that of induction-motor load. These conclusions are confirmed by measurements.

Power quality monitors are being installed in transmission and distribution networks all over Europe to collect statistics on voltage dips. Drawing up valuable voltage dips statistics is not as easy as it seems at first sight : the equipment of the network user is connected at a different voltage level, often behind a Dy transformer. The zero-sequence component is filtered out and the line and phase voltages are shifted. As a consequence the network user does not experience the same dips as recorded by the power-quality monitors in the network.

In Paper 2.50 (BE), a method is described to obtain valuable information on voltage dips with the commonly used monitors that do only record the r.m.s. voltages during the dip. The dip type and voltage phasors are derived, making it possible to take into account the way the dip propagates through the HV/MV transformer (see also Paper 2.59).

The approach can be used for statistical purposes, e.g. to obtain dips statistics for the phase-to-phase voltages from phase-to-ground measurements or to remove the zero-sequence out of the measurements. The algorithm can also be applied to compare the measurement information obtained from monitors installed at different voltage levels or with different connections (star and delta) and to obtain information of the dip as experienced by customer equipment.

The limitations of the described characterization algorithms should be taken into account when choosing the connection mode of the monitor :

- It is not possible to derive the phase voltages from the line voltages (the zero-sequence voltage is missing). Therefore, it is recommended to connect the monitor equipment in star in directly grounded systems (to record the phase-to-ground voltages).

- In impedance grounded systems, the zero-sequence impedance differs strongly from the positive and negative-sequence impedances and the results from the algorithm become questionable for two-phase-to-ground faults. A connection in delta might then be preferred (although two-phase-to-ground faults are only a minority).

Table 1: Summary of the three-phase unbalanced dips 
depending on fault type and location

|  | Fault Type | Dip Location |
| --- | --- | --- |
|  |  | I | II | III |
|  | 3-phase | A | A | A |
|  | 3-phase-to-ground | A | A | A |
|  | 2-phase-to-ground | E | F | G |
|  | 2-phase | C | D | C |
|  | 1-phase-to-ground | B | C | D |
| Type A: |
| Three-phase fault |  |
| Type B: |
| Single-phase fault |  |
| Type C: |
| Two-phase fault (or secondary type voltage dip, e.g. single-phase fault as seen behind a Yd or yD transfo) |  |
| Type D: |
| Secondary type voltage dip, e.g. two-phase fault as seen behind a Yd or yD transfo. |  |
| Type E: |
| Two-phase-to-ground fault |  |
| Type F: |
| Secondary type voltage dip, e.g. two-phase-to-ground fault as seen behind a Yd or yD transfo. |  |
| Type G: |
| Secondary type voltage dip, e.g. two-phase-to-ground fault as seen behind a YNy, Yyn, Yy or Dd transfo |  |

Paper 2.60 (ES) presents an interesting approach for the characterization of voltage dips, based on the extraction of significant features. The process is composed of five steps (Figure 9).

Figure 9:  Functional steps for the identification process

It is possible to train the classification tool (knowledge-based system).  It helps to determine the location and possible cause of the voltage dip, addressing the restoration plan and preventing some kinds of events in the future.

In a similar way, Paper 2.62 (BR) analyses two methods to estimate the so-called short duration voltage variations (SDVV) in electric power distribution systems.

One can distinguish two different cases :

- Systems in which monitoring sites are located in many network busses (transmission and subtransmission systems). The main parameter for estimation is then the voltage.

- Systems in which the monitored site is located at the supply bus (primary feeders, PQ-meters located in the substation). In this case, both voltage and current are important parameters for the SDVV estimation.

The developed estimators allow for the evaluation of SDVV indices in any given location, from a limited number of monitored sites.

Moreover, the fault location algorithms provide useful information for operation crews, which can considerably improve the overall quality of service by reducing restoring times.

Question 8

8.1	Is the classical characterisation and classification method for voltage dips (in terms of depth / duration) satisfying? Should other characterisation techniques – such as described in Papers 2.50 or 2.60 – be preferred, among other things in terms of predicting equipment sensitivity?

8.2	What are the actual practices of counting voltage dips and short interruptions for contractual purposes? Are there any comments or significant experiences concerning the way of defining ‘events’, the aggregation procedures and dealing with complex events?

8.3	On the other hand, what are the actual practices for system benchmarking purposes? Is the use of global indices (such as SARFIx) common practice? What kind of statistical processing is usually performed for system characterisation regarding voltage dips and short interruptions?

## Immunization techniques

Paper 2.45 (ES) explains that, basically, there are two immunization philosophies: leaving the plant with a controlled stop trying to restart after the dip, or keeping the plant working during the dip. In both cases, the “brains” (control systems) of the plant must go on working. As the total associated power is usually low, the UPS costs are very low as well, especially if there is a separated feeding system for controls in the plant.

To implement any one of the two immunization philosophies, there is a need to combine a set of tools:

- Temporized undervoltage relays

- UPS

- Time and level protection sets

- Special programs in “brains”

- “Ride through” features in static converters.

Most of them have a very short payback time, but it is important to take care of voltage dips since the beginning of the plant project.

Immunization techniques can be considered very locally (i.e. close to the key sensitive devices) or more globally (immunization of an entire process or plant).

Paper 2.46 (ES) gives a thorough description of the classical ASD (adjustable speed drive), being very largely used in the industry.

The sensitivity of these devices to voltage dips and short interruptions is clearly investigated and some local immunization techniques are reviewed:

- methods with additional energy storage,

- use of a boost-converter,

- active front-end rectifier.

Paper 2.44 (IR) reviews the available technology for global immunization. FACTS equipment can be used for solving stability or reliability problems in transmission system, but also offer some opportunities for utilities to provide adequate voltage quality and supply reliability, and for customers who can ensure adequate power quality inside the plant (Figure 10)

The ongoing deregulation in electrical energy transmission and distribution should push the development and the application of these new technologies.

| Name | Topology | Preferred Tasks |
| --- | --- | --- |
| Transmission | Distribution |  | Transmission | Distribution |
| STATCOM (Static Synchronous Compensator ) | DSTATCOM ( Distribution STATCOM ) | ESS: Energy Storage System | voltage control oscillation damping reactive power regulation | flicker compensation reactive power compensation harmonic filter |
| SSSC (Static Synchronous Series Compensator ) | DVR (Dynamic Voltage Restorer) |  | power flow transient stability oscillation damping | dip/swell compensation |
| UPFC (Unified Power Flow Controller ) | UPQC (Unified Power Quality Controller) |  | STATCOM and SSSC advantages | under voltage / over voltage compensation DSTATCOM and DVR advantages |
| Direct Current Transmission & HVDC Light System |  | power flow reactive power control in connected AC networks interconnecting asynchronous networks | coupling of remote loads or remote energy sources optimization of energy cost through coupling of bus bars or system parts |

Figure 10: FACTS equipment in transmission and distribution networks

An original proposal of global immunization is described in Paper 2.49 (IT), mainly for non-industrial utilities. It starts from the fact that many users choose to enhance Power Quality by using uninterruptible power supply (UPS) units, generally provided with a DC section containing a storage system. In addition, recent technological developments made smaller generators available (in the order of the tens of kW) that can be interconnected to the distribution network. Some of these, such as photovoltaic arrays and fuel cells, generate DC current; others, such as micro-turbines, need an interface converter with a DC stage for their connection to the network.

The increasingly widespread use of DC current, both in the generators and in the electrical equipments, leads to the possibility of integrating the various devices by means of a local DC distribution system (Figure 11). Moreover, the use of DC current makes it possible to transmit higher power, with the same conductors. Lastly, by means of suitable control strategy, it would be possible to share the load among the various sources of supply (utility and, if any, the generators and the storage systems embedded in the DC local network) in such a way as to achieve optimization both of the use of primary energy and of power exchanges with the public network.

Figure 11: Comparison between distribution in direct current (a) and alternating current (b).

Question 9

9.1	Adjustable speed drives (ASD) obviously belong to the most sensitive industrial devices, for voltage dips. What are the local desensitisation methods specific for this type of loads? How often are they used and what is their efficiency?

9.2	Are there any experiences of using active conditioners for global – large power – disturbances mitigation in industrial environment? Are these experiences always satisfying? Are partnerships usual between utilities and some of their customers for the installation and the management of such systems?

9.3	Is DC distribution considered today as a realistic alternative towards “high quality” networks? Are there any practical experiences or projects to mention? What are the actual technological trends in this direction?

## Techno-economical assessment

Paper 2.53 (BE) compares various systems protecting industrial processes against voltage dips: Flywheel, Static UPS, Dynamic Voltage Restorer (DVR), STATCOM, Shunt connected Synchronous Motor, Boost Converter, Active Front End (AFE) and a Transformerless Series Injector.

It is concluded that there is no single system superior in all situations :

- Installing a boost converter, an AFE or a DVR without energy storage is most appropriate if the processes to be protected include a DC-bus that can be reached from outside. The boost converter has the advantage of having negligible losses; the AFE and the DVR have other capabilities such as drawing a sinusoidal supply current or the ability of supplying reactive power.

- For processes that do not have a DC-bus, a DVR (still without energy storage) or a transformerless series injector are generally cost effective. If harmonics and reactive power also cause problems, the shunt-connected synchronous motor could be considered.

- The percentage of outages being prevented by a certain solution cannot be predicted without statistical dip data. If all dips and short interruptions have to be mitigated, the only possible solution is installing a flywheel or a static UPS.

The paper finally refers to a method in order to analyze whether the expected reduction in outage cost outweighs the cost of the protective equipment. The following adapted version of the Net Present Value method is suggested:

where

Cinv	initial investment per kVA,

f 	annual outages due to dips,

pprev	percentage of outages being prevented,

f·pprev	annual mitigated outages,

Cdip	outage cost per dip per kVA,

pmnt	maintenance costs per kVA per year as a percentage of Cinv,

i	discount factor,

n	project time.

By introducing numerical values for a mitigation system (e.g. Cinv= €100/kVA, pmnt=0, pprev = 100%), this formula can be used to determine whether the reduction in voltage dip losses will outweighs the cost of the mitigation devices.

Paper 2.54 (ES) defines a methodology that allows to select the most suitable topology for a single-converter based Voltage Dip and Outage Compensator (VSOC). The evaluation of a suitable topology should consider all the components such as the electromagnetic elements, energy storage devices, static switches, filters and others. Single-conversion topologies (Figure 12) improve the efficiency, reliability and maintenance cost of the well-known double-conversion based UPS systems.

Figure 12:  Generic Single Conversion Topology (SCT)

The proposed methodology is based on the computation of the so-called “coefficients of use”. Each family of elements (semi-conductors, inductances and capacitors) has its own coefficient. These coefficients show the ratio between the power of each family of elements and the overall power of the protected load. Adding appropriate cost coefficients, overall cost can be computed.

In order to complete the selection of the most suitable topology, two important aspects should be evaluated and compared as well: the time response of the compensator (or dynamic behaviour) and the reliability of the system.

Question 10

10.1	What is the methodology for assessing the cost of voltage dips effects in industrial installations?

10.2	What is the methodology for choosing the optimal mitigation solution, from the combined technical and economical point of view?

10.3	Do we have significant figures to quantify the costs associated with “non-quality” in industrial cases?

## Voltage dip related industrial power quality problems

(experiences and case studies)

Paper 2.43 (EG) presents the results of a Power Quality survey audit performed at AEDC (Alexandria Electricity Distribution Company).

It provides guidelines for customers in developing equipment specifications and performing economic evaluations of power conditioning mitigation requirements.

Paper 2.48 (PT) presents the results of studies performed for four EDP industrial customers that reported PQ problems. The voltage supplied to the four customers is perfectly in agreement with the requirements of the EN 50160 standard, but the problems came from the sensitivity of some equipment to voltage dips.

Paper 2.57 (SE) summarizes a joint project to reduce Power Quality related costs for the Swedish Pulp&Paper (P&P) industries.

PQ-audits were performed at all the selected industries and utilities, collecting information about the technical and economical consequences of bad power quality, immunity requirements for sensitive devices etc.

Some specific technical issues are addressed such as:

- Voltage dips propagation

- Network solutions : fault current limiters, line-arresters or sky-wires grounding.

Paper 2.55 (PL) describes the major results of a project aiming at collecting data on attitude, opinions and preferences as regards power quality, electrical safety and functionality, for industrial consumers in Central Europe. End users have serious power quality problems and only a few sites did not experience any problem at all.

The users are not adequately trained in solving this category of problems and big differences appear between countries.

Paper 2.58 (MY) discusses the concept of power quality program aiming at reducing voltage dip incidences. Techniques are to be selected on a case-by-case basis to avoid ineffective solution.

# IV	Power Quality in the competitive market

## Context

Deregulation introduces a clear business separation between energy suppliers and network operators. New types of companies, called the “Distribution Network Operators” (DNO), are responsible for the secure distribution of electricity to the customers and facilitation of fair competition.

In this general context, guaranteeing acceptable Quality of Supply belongs to their tasks as well. As discussed in Paper 2.70 (ES), Quality of Supply is considered today as having three major components: energy supply reliability (voltage continuity), voltage quality (mastering the disturbance levels) and “commercial” quality (linked to the quality of the customer relationship and the customer satisfaction).

Among the constituting parameters of Quality of Supply, voltage continuity is obviously the first one being systematically taken into account in regulations or contractual applications. On the other hand, there is no general consensus on the definition of “acceptable” quality and the way in which regulating authorities allow DNO to include quality aspects in their tariffs differs from country to country. Targets and incentive/penalty regimes are being considered progressively.

Finally, although being responsible for the quality delivered to the end-consumer, DNO are also depending on the quality available at the upper stage, the Transmission networks level (operated by the TNO).

The sharing of responsibilities between DNO and TNO on reliability is discussed in Paper 2.63 (AR). Power system reliability breaks down in two components: adequacy and security. Adequacy is the long-term – or steady-state – reliability : there is enough capacity to generate and transmit the power to meet the demand at any time. Security is reliability in the short-term, and relates to the ability of the system to react to disturbances. The actual Argentinean regulatory framework does not distinguish between adequacy and security issues.

Adequacy problems in transmission may be solved by suitable network expansions. This responds to market incentives, while solving security problems is not necessarily driven by the market. Security problems are highly unpredictable, and rarely giving way to specific expansions of the transmission network. With the current Argentinean regulatory frame, the authors fear that the overall reliability will not reach levels comparable to those of countries where networks have developed along many years.

## Benchmarking utilities

By its very nature the distribution of electricity is a natural monopoly and there is a need for benchmarking. Electricity regulators are focusing increasingly on the measurement of outputs such as continuity of supply, in addition to the control of revenues. Using information from OECD countries, Paper 2.78 (UK) examines the fundamental linkages between continuity performance (average frequency and duration of long supply interruptions) and network characteristics, as well as the methods used by regulators to set quality targets.

In the classical IEEE terminology, the three basic quality indices are :

-	SAIFI (System Average Interruption Frequency Index) : yearly average number of interruptions per customer,

-	CAIDI (Customer Average Interruption Duration Index) : average duration of interruptions (min/interruption),

-	SAIDI (System Average Interruption Duration Index) : yearly average duration of interruption per customer (min/customer/year),

the third index being the product of the two first ones.

Benchmarking is however difficult because :

-	quality indices depend on the way in which outages are recorded (interrupted power and duration give ENS – energy not supplied – the only possibility in HV systems and probably the best method ; some DNOs record ENS from the nominal power of the disconnected transformers ; others make an estimate of the number of interrupted customers from average numbers of customers per transformer ; others really count the number of interrupted customers ; etc.) ;

-	depending on the way in which the indices are estimated and on local use, the same indices may have a lot of different names (SAIFI may be called "CI", "IF", "NIEPI", "interruption frequency", etc. ; CAIDI may be called "interruption duration", "average duration", etc. ; SAIDI may be called "AIT", "CML", "IC", "TIEPI", "AOTC", "supply unavailability", etc.) ;

-	only "long interruptions" are to be taken into account to assess the voltage continuity ("short interruptions" are considered as a voltage quality problem, in the same way as voltage dips) ; however, the time limit to discriminate between "long" and "short" interruptions is somewhat arbitrary (3 min for EN 50160, 5 min for IEEE P1366–2000, 1 min in Australia and New Zealand, 3 min instead of 1 min in UK since April 2001...) ;

-	interruptions due to severe weather conditions, load shedding, transmission interruptions, pre-arranged outages or LV outages, etc., are or are not excluded from statistics, according to local practice.

As a consequence the availability and quality of data on continuity of supply performance is found to vary and there is a need for international recommendations – as expected from the Joint CIGRE/CIRED Working Group on "Power Quality Indices and Objectives" (Paper 2.74).

Furthermore, any benchmarking method should provide means of normalizing the results. Different measures of load density or customer/circuit utilization may be considered, GWh/km², MWh/MV-km, Customers/km², Customers/MV-km... Whilst more data are available for the load density comparison, the customer/circuit utilization comparison may provide a closer reflection of the effect of MV circuit lengths and hence topography of the networks.  Both comparisons show however that there is a general consistency between reliability and load density.  The use of the energy not supplied (ENS) instead of the number of interrupted customers, may also give some weighting to commercial and industrial customers which would otherwise be absent in purely customer weighted comparisons.

A performance normalization model seems to be needed and a proposal is described in Paper 2.67 (UK), making a distinction between the key factors, being inherent (demographic features, customer density, topographic features, geography of the service areas including weather, tree cover, geology etc., traffic congestion), inherited (network designs – size, length, overhead/underground) or incurred (linked to operational practices).

The key factors not linked to operational practice are : customer density, circuit length and overhead line proportion of the circuits. Moreover, these three factors are of two different types. Circuit lengths and the percentage of overhead lines in the circuits are network-oriented factors while customer density is a customer-oriented factor. This indicates that a two-step disaggregation and performance normalization model should be considered.  Such a model would initially use the network-oriented factors and the customer oriented factor separately.  The model would then allow the combining of the results from the two steps possibly using some weighting coefficients.

The influence of inherent, inherited and incurred factors is illustrated in Paper 2.78 (UK) by considering the disaggregation of the system average interruption duration index :

The “customer(minutes” term can be divided into those minutes lost due to planned outages and those due to faults.  A high level of minutes lost due to planned outages for example may indicate significant work being carried out on the network, particularly where there are limited means of providing an alternate supply.  However live working techniques and the provision of standby generators should mitigate planned outages.

The term “customer(minutes per km of network” indicates that part of the performance of the network over which the distribution company has control (inherited and incurred factors), whereas the term “km of network per customer” reflects the inherent factor of geography (population density) that the distribution company cannot control.

Further disaggregation of the term “customer(minutes per km of network” is possible, leading to:

The range of ratios of customer(interruptions to faults (namely the average number of customers affected by a fault) reflects system configuration and protection policy (inherited factors which a company may ameliorate in the longer term). Reducing this ratio requires investment to increase the number of circuits and/or protected zones, including investment in switchgear, protection equipment, auto-sectionalizing and remotely controlled switching.

The fault rate (faults per km of network) reflects construction and condition of assets as well as the weather conditions encountered. Fault rates are therefore influenced by inherited and incurred factors (although it may be argued that severe weather is inherent).

Additional information on this subject is to be found in Papers 6.7, 6.26, 6.31, 6.42 and 6.54 (see the section on Power Quality related Papers in other Sessions).

Question 11

11.1	The quality levels that are imposed today by the regulators seem to be mostly characterised by indices related to service continuity. Is this a general trend? Should indices be added, concerning more precisely the voltage quality? Are there some proposals or concrete experiences in that field?

11.2	As far as service continuity is concerned, a disaggregation can be made on the basis of various parameters. Is this justified and usually accepted by the consumers? Should a similar differentiation also be made for indices related to voltage quality?

11.3	What are the actual practices concerning the sharing of responsibilities between distribution companies and transmission grid operators, for guaranteeing quality levels?

## Obtaining and analysing reliability data

Reliability data collection is essential for quality reporting. Furthermore, the statistics provide the input data for reliability studies, predicting the damage for customers or penalties to be expected with new network designs or new operational procedures. The results are to be compared with the costs or savings involved. The collection of quality parameters should not be seen only as an obligation toward the regulators, but first and foremost as an opportunity to guide investments, while reducing costs.

Paper 2.72 (IT) shows how quality indices can be calculated from a wide range of data contained in several databases. It is necessary to create an integrated system capable of drawing the information available from the various systems available within the company (GIS, SCADA, planned interruptions information…), see Figure 13.

Figure 13:  Integrated system showing databases interaction

The supply state of all customers, from HV to LV, is continuously monitored to accurately determine the voltage continuity indices.

The report stresses that thanks to the use of statistics, maintenance activities in the distribution system have been better targeted. Investment planning has also undergone significant changes and has enabled focused interventions on critical assets, as highlighted by the quality indices.

In a similar way, Paper 2.73 (DE) describes the new outage statistic system of an Austrian distribution system operator (VKW) :

- The data describing the sequence of MV outage events is extended to include the end of the event, giving an important input for probabilistic reliability analyses.

- An automatic allocation of individual network components to the separate outage events is implemented. The failure performance of the system can then be checked for geographical and component related data. This information is important for the prioritization of maintenance and re-investments.

Figure 14: Outage data registration process

Paper 2.76 (BE) describes a simple computational approach for the evaluation of supply unavailability (SAIDI), based on the performance of all network elements being treated statistically. The impact of the network structure is highlighted and the positioning of circuit breakers, automatic devices, remote controls, feedback loops, etc. is quantified in terms of extra minutes of availability.

The study was done without the help of any specific software ; simple calculations were based on a method described by the UNIPEDE (now EURELECTRIC) DISQUAL 50.05 experts group.

Paper 2.69 (CZ) gives thorough examples of reliability analysis. The authors suggest using the principles of non-linearity (i.e. in some cases there is no linear dependence between the length of a feeder and its rate of failure), non(homogeneity (components of the same type do not show similar behavior as to failure rate) and respect for the time factor (there can be a change in failure rate in time, when considering periods of ten years of observation). These principles may be applied for the analysis of statistical data of equipment failure rate, for evaluating the continuity of electricity supply to consumers, as well as for calculating the reliability of electricity supply for future consumers when developing the network.

Supply restoration time may be reduced by use of remote control equipment as demonstrated in the paper. The so-called sequential trend characteristics (see an example in Figure 15) evaluate, year by year, the percentage of restored supply within a given restoration time.

Figure 15: Trend characteristics of supply restoration times 
on 22 kV supply cables. In 2000, for example,
80 % of outages lasted less than 30', 30 % less than 6'.

As an alternative to global monitoring, Paper 2.80 (AR) presents the control of service quality by sampling measurements, from which global indicators can be obtained. A great experience is necessary to suitably correlate the results of the sampling with those obtained by the conventional method. The sample size must not be lower than 300 items per layer (this one being either all the network, or a voltage level, or a geographic zone, etc).

Question 12

12.1	What are the actual practices in order to collect reliability data and compute the reliability indices? What are the most frequently used indices? What are generally the requirements of the regulating authorities?

12.2	Do DNO use some dedicated software to analyse and predict the reliability of their network and study the influence of the network structure, planning and development strategy? Which software is used?

12.3	Are there any other experiences of systematic sampling measurements in order to have a statistical assessment of the reliability and/or quality? Which kind of sensor or measurement device is then used? What are the major technical problems associated with this practice? What are the statistical constraints? What are the costs?

## Power Quality monitoring

Power Quality monitoring has become a basic practice, required for many technical reasons (technical problem troubleshooting - see section III of this report -, technical management of the system, investment and planning purposes), marketing reasons (care policy towards the customer) and liability reasons (reporting towards Regulation Authorities).

Paper 2.59 (FI) develops the concept of power quality management as an essential part of a comprehensive Distribution Automation (DA) system. Usually, power quality data acquisition, storing, and reporting are separate stand-alone applications, which are not integrated as part of the DA concept.

The paper addresses :

- Integration and interfaces between utility’s information systems (distribution management system, AM/FM/GIS network information system, SCADA, customer information system)

- Web-based applications for Internet and Intranet users.

Considering basic analyses and measurements the paper focuses on voltage dips : phase-to-earth measurements, dips in phase-to-phase voltages, extracting phasor information from r.m.s. voltages, transfer of dips and effect of transformer connections (see also Paper 2.50).

Similar concepts are discussed in Paper 2.26 (US) explaining that the new utility environment requires availability of state-of-the-art protection, control, monitoring and recording systems, that are easy to install and maintain. Such systems take advantage of the advanced functionality of multifunctional protection and monitoring/recording IEDs (Intelligent Electronic Devices) with communication capabilities. At the same time, the availability of utility communication networks and the use of off-the-shelf Web technology makes the data and information from the IEDs easily available to different utility clients using standard Web browsers. Power quality monitoring and recording functions in specialized devices, multifunctional protection IEDs and the substation HMI (Human Machine Interface) provide an integrated cost effective and at the same time reliable solution.

However, there is still much work to do in order to converge to universally accepted and used quality indices. In the actual deregulation context, the joint working group CIGRE/CIRED "PQ Indices and Objectives" was formed in 2000.  The starting point of the working group activities is the evaluation of the indices and objectives proposed in the IEC technical reports 61000-3-6/7 concerning harmonics and flicker, with a possible extension of these concepts to voltage unbalance.  Additionally, the working group is discussing indices for the fault-related PQ aspects, namely voltage dips and interruptions.  Measurement data are collected in order to provide a reference basis for the future recommendations. The status of the works is given in Paper 2.74 (CA).

It seems that the presently recommended planning levels for harmonics and flicker in HV network are somewhat restrictive : higher levels were frequently measured, without known interference problem.

Paper 2.61 (AU) focuses on transient phenomena indices, for which no standard is available. A Transient Severity Indicator should be a single number for each transient event, related to the degree of severity to customers. A Transient Site Index should be the sum of all transient severity indices, scaled to an agreed survey period, usually one year.

Present transient event characterization practices such as ITIC overlays do not lead to an adequate comparison of sites for their transient severity. The ITIC count approach does not distinguish transient events which are closer to the ITIC curve from those which are far from it. The V2t transient index offers an attractive way of characterizing transients and ranking sites for their transient severity (Figure 16).

Figure 16 : V²t=40 fit on v-t plane of ITIC curve

Power quality monitoring is known to produce a large amount of data which has to be converted in information. Without automation, the monitoring of a complete distribution network would be nearly impossible. Additionally, the extracted information must be tailored to the needs of the various consumers of it. Three levels of PQ reporting have been identified as necessary in Paper 2.42 (AU): site (problem solving or engineering analysis), network (group of sites), and utility (reporting to the regulator).

These levels of reporting encapsulate two key requirements for a PQ data framework, namely time compression and space compression. The former is concerned with the reduction of long time series of a specific measurement into a single number while the later is the reduction of the same measurement taken for several locations into a single number to characterize an area. Another important requirement is the easy navigation between the various reporting levels so as preserve the tractability of all data to the original measurements. The complete PQ data framework, also named PQ data triangle, is shown in Figure 17.

Figure 17: Power Quality triangle

Following Paper 2.42 (AU), the usage of XML brings several benefits. The ease of data sharing through text files makes these data independent from computing platforms and prevents rapid obsolescence. Since XML is largely used, the integration of the PQ framework into other schemes will be simplified.

Examples of quality monitoring results are given in various papers: 2.52 (CA), 2.65 (EG), 2.71 (RO), 2.77 (NL) and 2.81 (AU). The second and third papers are also focusing on techno-economical issues concerning the cost of disturbances in consumer premises, the optimal cost/quality ratio and the cost aspects of the quality monitoring activities themselves.

A simple method of ranking sites is shown in Paper 2.81 (AU) for selecting sites where PQ monitors should be best installed. The Voltage Disturbance Figure (VDF) is calculated by assigning equivalent lengths to each part of the distribution system including overhead lines, transformers, etc., weighted by the loading. The calculation is similar to a load flow but much simpler.

A new line mounted current monitoring device utilizes the magnetic field produced by the current flowing in the conductor. It is depicted in Paper 2.82 (SE). The use of the magnetic field as a primary power source means that batteries are not necessary, and therefore minimal maintenance is required. The sensor is mounted directly on the line and communicates via a built-in radio transceiver.

Figure 18: Line mounted sensors

The benefit of the system is its ability to pinpoint a fault in the network, from 1 A upwards, below the protection threshold. It can warn of initiating faults, and provide a predictive monitoring service. The sensor is mounted at intervals of approximately 1.5 km. It can also provide line loading information for capacity planning, and valuable information regarding power factor, system design parameters, and phase balancing.

A cost-benefits analysis (based on the Swedish Network Regulator Model) gives a pay back time between 3 and 6 years on the investment, for the monitoring of the studied test network. Taking the valuation of customer satisfaction into account (still by the method of the Swedish regulator), a pay back on investment of only one year is expected.

Question 13

13.1	Procedures have been introduced within IEC for the assessment of voltage quality with relation to harmonics and flicker (IEC 61000-3-6 and 61000-3-7). Beside these recommendations and the standard EN 50160, which standards and criteria are the most frequently referred to, for characterising the voltage quality? What are the actual reporting practices?

13.2	Is there any methodology to choose the location of Power Quality permanent monitoring devices?

13.3	Are Power Quality state-estimation techniques used in complement of monitoring devices, in order to limit their amount while giving an overview of the quality?

13.4	Is there a trend do develop Power Quality monitoring as a stand-alone system or rather to integrate it within a more general Distribution Automation context? In Energy Meters ? What are the technological possibilities?

13.5	Do we have examples of cost-benefit analysis of Power Quality monitoring?

## Customer relationships

(the role of system operators and energy service companies)

According to Paper 2.66 (DE), the investment programs of the German system operators are significantly reduced. The medium and long-term effects of this on the level of supply quality remain to be seen. It seems certain that customized solutions for satisfying customer's demands on supply quality will gain in significance. In the modern "digital society", more and more installations react very sensitively to voltage dips in the millisecond range.

Typical network solutions are usually proposed to customers having the primary concern of avoiding power supply interruptions. These are no longer sufficient. However, the use of new technical solutions should be preceded by considerations of the possibilities to "desensitize" critical components within the customer's plant. Increasing the reliability of the whole system is not a suitable reaction to compensate a lowering of immunity of individual devices and plant components.

Considering the pressure on charges for system use as a result of the market liberalization, a rise of the value of supply quality is not to be expected. On the other hand, the increased application of automation and other advanced technologies by customers is calling for individual solutions tailored to specific quality requirements. The intensive discussions of possible technical solutions must always be accompanied by corresponding considerations of the economic aspects, whereby a final decision must satisfy both interests.

Services to satisfy tailor-made demands on quality of supply are thus becoming an ever more central topic for today's energy service companies.

Papers 2.68 (BE) and 2.79 (IT) give surveys of the most frequently encountered and the most typical problems in industrial networks, together with the available solutions.

At present, most energy-intensive sites suffer to a certain degree from poor power quality, while most sites have already adopted some solutions. This is typically purchasing of a UPS, back-up generator, adoption of true-r.m.s. measurement and complemented with some of the other solutions, such as meshed earthing, TN-S rewiring, active conditioners, etc.

It is unlikely that a single solution will be effective. Careful design of a solutions mix, tailored on the PQ problems experienced, and based on a detail understanding of the causes of the PQ problems is needed.

Outages and interruptions are still the most visible problems. A susceptibility of processes to events with a duration even less than 1 second has been ascertained for 80% of respondents to the enquiry presented in Paper 2.79 (IT).

PQ monitoring equipment has still a very small penetration rate in the sample. Moreover the percentage of customers keeping a log of PQ disturbances’ occurrence is also small, thus demonstrating the need of larger information for end-users.

Costs attributed by users to PQ problems have been investigated by using both direct costing and contingent valuation methods. The latter asks customers how much they would be willing to pay to avoid an event with consequences on the production process ; about 80% of respondents stated that they would pay nothing for that ; the remaining 20% responded they would pay up to 5 EUR/kW (annual peak demand). Nevertheless, for the majority of respondents, the cost attributed to PQ disturbance consequences on the process results to be between medium and very high. Additional information on this subject is given in Paper 6.31 (see the section on Power Quality related Papers in other Sessions).

Paper 2.75 (BE) describes the Leonardo Power Quality Initiative (LPQI), a EU supported continuous learning project for professionals dealing with electrical installations. This project intends to provide education on Power Quality topics intended for end-users.

Surprisingly, in spite of the huge losses caused, PQ has failed to become a major topic in industry in most European countries.

The European LPQI project intends to fill an apparent knowledge gap for professionals increasingly encountering PQ-related problems. They can learn about this subject by dedicated application notes or go through an e-learning process at any time at their own speed, possibly leading to a certificate.

Question 14

14.1	Do DNO usually propose “high quality” supply schemes to sensitive consumers? What about the concept of “Premium Quality Park”? Should such contracts be offered by electricity suppliers or by system operators? Who has the final responsibility for the quality?

14.2	Are customers willing to pay for enhanced quality?

14.3	Are mitigation systems available for very important power levels? Which “network oriented solutions” are used up to now? Are there specific tools for their implementation and evaluation? What are the future trends?

14.4	Is a rise of the basic value of supply quality in the electrical power supply systems to be expected, in the actual deregulation context? Will DNO be allowed to include a quality-linked component in their tariffs?

14.5	Efforts to assess customer's interruption costs are reported in Papers 2.79 and 6.31. Are estimates available in other countries for long interruptions – notified or non-notified – in EUR(orUSD)/kWh, for short interruptions and voltage dips in EUR(or USD)/kW?

14.6	Is it thinkable that other criteria such as the customer satisfaction could be taken into account?

14.7	Are customer enquiries frequent? What are the most frequently encountered remarks?

# Power Quality related Papers in other Sessions

Papers 3.10, 3.12, 3.35, 4.28, 4.39, 4.59, 6.7, 6.22, 6.26, 6.31, 6.42 and 6.54 include interesting information concerning Power Quality and could have been included in Session 2

Paper 3.10 (BE) presents the quality module of a SCADA / DMS (Distribution Management System). Two main concepts are considered :

-	Power outage forecast : every foreseen operation on the network is simulated in order to assess the consequences in terms of affected busbars and unsupplied customers.

-	Incident management : every incident that occurred in the network may be replayed and simulated.

Moreover, quality criteria are generated : e.g. Average Outage Time per Customer (AOTC – or SAIDI), distribution in several predefined categories by number of outages, by duration of cuts, etc. A "decomposition criterion" enables to make some computations distributed by municipality, sector, area, voltage level...

Paper 3.12 (CA) describes an application of knowledge engineering for the evaluation of voltage continuity. The system is able to perform comparative studies using, for the same set of lines, different assumptions of equipment used and of intervention strategies applied. It calculates quality indices for every studied scenario : the IC index (or SAIDI) giving the system average time of interruption by customer ; the IF index (or SAIFI) giving the system average frequency of interruption by customer.

Paper 3.35 (ES) presents an integrated solution for the Quality of Service system with real time connection to the DMS. This system provides both real time and historic reports, for all voltage levels, with web based interface. Quality indices are established by region, province, town... (outages, planned interruptions, etc.). This includes TIEPI (Interruption duration weighted by the installed power – or SAIDI) and NIEPI (Number of interruptions weighted by the installed power – or SAIFI), according to the Spanish Regulation. Discounts can be applied on customer bills depending on the quality they have been given during the year.

Paper 4.28 (DE) presents the five main converter types for wind energy (Figure 19) and analyses the power quality behavior of two of them (the double-fed asynchronous generator and the inverter coupled synchronous generator). Flicker and harmonics are important at the LV side but considerably reduced at the MV side of the transformer.

Figure 19 :  Mainly used wind energy converter types

Paper 4.39 (DE) stresses that inverter-based generators offer the possibility to serve as UPS and/or filters, thus improving power quality (Figure 20). However, many inverters used for photovoltaic generators produce a strong signal in the frequency spectrum around 15.75 kHz (about 0.6 V to the mains voltage 230 V), which is situated outside the frequency range regulated by standards. This shows the need for limit values in the frequency range from 2 kHz to 150 kHz.

Figure 20 :  Reduction of harmonics in LV,

measured with 3 kVA self-commutated inverter

Paper 4.59 (DE) shows that dispersed generation (MV & LV) close to the customer, along with storage units (MV & LV) and power exchange between systems (MV) may be a good alternative (economically and ecologically) to network enhancement for providing higher levels of power quality. Power exchange between galvanic separated networks is possible via MVDC couplers (Medium Voltage Direct Current) using IGBT elements (Figure 21). A decentralized energy management system (DEMS) ensures optimization depending on weather and load forecast.

Figure 21 :  Principle of a MVDC Coupler

Paper 6.7 (GB) comments on the new quality of service incentive scheme which was introduced on 1 April 2002 by Ofgem (the British Regulator) :

-	A mechanism that penalizes DNOs annually (up to 1.75 % of revenue) for not meeting their targets for the number and duration of interruptions. There is also a rewarding mechanism for companies that exceed their targets, based on the rate of improvement by 2004/05.

-	A mechanism for rewarding or penalizing companies annually (up to 0.125 % of revenue) depending on the quality of telephone response they provide to customers.

A consequence is the necessity to develop a robust reporting and audit framework for quality of service information (see examples of results in Figure 22 and Figure 23).

Figure 22 :  Cumulative frequency plot for the number of customers affected by interruptions at all voltages (sample size: 150)

Figure 23 :  Cumulative frequency plot for the duration of interruptions at all voltages (sample size: 100)

Paper 6.54 (GB) comments on the same scheme and addresses the problem of understanding when inadequate performance comes from controllable factors and when it is a consequence of inherited or inherent factors beyond managerial control. Disaggregation is then needed so that performance in each group becomes comparable across DNOs. Ofgem offered a conclusion that factors that should be accounted for are :

-	Demographic factors (Customer density),

-	Topographic factors / Network Design,

-	Severe Weather (this latter being automatically treated in the "exceptional events mechanism").

Over time, factors linked to demography are likely to be the primary comparison mode in the future when the relevance of inherited network design factors diminishes.

Figure 24 :  Year-on-year measures considered for incentives/penalties and percentage of distribution businesses' revenue put at risk for failing the service performance targets

Paper 6.22 (ZA) claims that Power Quality Forums between Utilities and Customers assist in keeping lines of communication open, leading to both intangible and economic benefits to all parties.

Paper 6.26 (DE) says that the most important grid is the MV one (it defines about 80 % of service availability and about 25 % of total network costs). Three 20 kV innovative technical approaches for increasing availability are described :

-	Condition and availability centered maintenance program of XLPE cables in order to reduce interruption frequency (SAIFI, CAIFI).

-	Operation of selected disconnectors via mobile phone modems in order to reduce interruption duration (SAIDI, CAIDI).

-	Use of fault distance location relays in order to reduce interruption duration (SAIDI, CAIDI).

Figure 25 illustrates the efficiency of the latter : currently, with 32 % of all feeders upgraded with such relays, grid performance with regard to non delivered energy per outage is about 25 % better compared to 1994/1995, although the number of service points has been reduced by approximately 35 % (20 kV grid). Note that the basic Zollenkopf criterion, that considers 60 MVA.min non delivered energy per outage as acceptable for customers, has always been respected.

Figure 25 :  Effect of digital distant relays with 
integrated fault position finders

(1) Zollenkopf criterion (MVA.min)

(2) ENS (energy not supplied) per outage (MVA.min)

(3) Number of service points with staff

(4) Percentage of feeders equipped with fault distance relays

Paper 6.31 (NO) reports on a national survey in Norway to assess Customer's Interruption Costs (CIC). Direct-worth (DW) and willingness-to-pay (WTP) estimates were obtained and the average of both values was chosen as the best estimate for CIC, leading to :

-	4.10 EUR/kWh for non-notified long interruptions (> 3 min),

-	2.96 EUR/kWh for notified long interruptions,

-	0.89 EUR/kW for short interruptions (( 3 min),

-	0.63 EUR/kW for voltage dips.

For Norway, the yearly summing up gives :

-	Long interruptions : 108 MEUR/year,

-	Short interruptions : 76 MEUR/year,

-	Voltage dips : 22-42 MEUR/year.

These results will be important in the evaluation of which power quality issues are to be regulated through incentive mechanisms, and which are to be regulated by means of standards.

Paper 6.42 (ES) presents the thresholds of quality of service which must be respected for every final customer in Spain. Table 2 shows the values for MV systems.

Table 2

The penalizations are five times the cost of the kWh in the tariff.

On the other hand, the economic level of quality of service for utilities is achieved when the marginal cost of providing the quality is equal to the marginal income, in other words, when penalizations equal the increase of investments and expenditures needed to avoid them. It is shown that the penalizations are high enough so as to guarantee that the system tends to the optimum. For Endesa, next year, the optimum ratio of investment by supplied energy will be 0.01 EUR/kWh.

# List of Papers

I	EMF, EMI, SAFETY

1	R. Hermes de Oliveira, R. Oling, AES Sul (Brazil)
M.L.B. Martinez, C. de Salles, A.D. Figueira, UNIFEI (Brazil)

Analyze of distribution lines class 25 kV under direct lightning strokes or lightning induced

2	A. Sumper, J. Rull, CITCEA - UPC (Spain)

##### Effects of overvoltages on the quality of supply

3	H.J. Jorgensen, DEFU (Denmark)

Risks incident to harmonics in compensated MV networks

4	A. Ametani, T. Okumura, Doshisha University (Japan)

Experimental investigation of a transient induced voltage to an overhead control cable from a grounding circuit

5	I. Zamora, A.J. Mazón, J.R. Saenz, University of the Basque Country, J. Amantegui, F. Antepara, Iberdrola(Spain)

Experiences of neutral resonant system implantation in Gorliz substation

6	K. Grabner, Elektro Ljubljana (Slovenia)
B. Cestnik, Electric Power Research Institute Milan Vidmar (Slovenia)

Installation of new power substations in the environment with regard of Slovenian non-ionizing radiation legislation

7	S. Bojic, A. Sekso-Telento, Z. Bertalanic, Energy Institute, G. Mihovilovic, Hidro-Watt (Croatia)

Overvoltage protection of small hydro power plant connected to Croation distribution network

8	H. Luternauer, D. Hearn, H.-H. Schiesser, Elektrizitätswerk der Stadt Zürich (Switzerland)

Electromagnetic fields - Optimisation of MV/LV transformer stations

9	N.A. Lemozy, M.S.F. Brugnoni, University of Buenos Aires (Argentina)

##### Propagation of transients in electrical distribution networks

10	Y. Rajotte, J. Fortin, B. Cyr, Hydro-Québec - IREQ(Canada)

A touch voltage measurement applicable on energized MV and LV lines

11	E. Alvarez Vazquez, Iberdrola Distribucion Electrica (Spain)

The regulatory framework for power line communications technology

12	J.M. Molina Nuñez-Lagos, Iberdrola Distribucion Electrica (Spain)

Legal actions regarding electromagnetic fields (EMF) - The spanish practical case

13	E. Zabala, J.E. Rodríguez, L. Rodr´guez, E. Perea, Labein Technological Centre (Spain)

Analysis of the perturbations due to disconnector switching in AIS substations based on measurements and simulations

14	A. Hammad, G. Blättler, NOK Baden (Switzerland)

Damping of low frequency resonance induced overvoltages in a distribution network

15	D. Fulchiron, J. Delaballe, Schneider Electric Industries (France)

Reduction of the low frequency EMF emission of MV/LV substations

16	K. Schilling, Siemens AG, S. Will, E.ON Bayern AG (Germany)

Reliability analysis of MV networks with different neutral earthing schemes

17	S. Schmidt, Siemens AG, R. Heitbreder, Volkswagenwerk AG (Germany)

Performance of industrial network improved by low resistance neutral treatment

18	H. Cheng, W. He, G. Lu, Shanghai Jiaotong University, G. Pan, J. Zhang, Shanghai Eastern Power Supply Bureau (China)

Evaluation of risk influence from power cable to communication line in TRANSRAPID Shanghai

19	G.V. Podporkin, V.E. Pilshikov, A.D. Sivaev, M.K. Yarmarkin, Streamer Electric Company (Russia)

Lightning protection of power médium voltage overhead lines with covered conductors by antenna type long flashover arresters (ALFA)

20	L. Grcev, A.P.J. van Deursen, Eindhoven University of Technology, J.B.M. van Waes, Holland Railconsult,
F. Provoost, M.J.M. van Riet, B.V. NUON (Netherlands)

High frequency current distribution at HV tower with GSM system between earth wires, tower grounding and LV/MV cable network

21	J. van Waes, A.P.J. van Deursen, Eindhoven University of Technology, F. Provoost, M.J.M. van Riet, NUON TPC (Netherlands)

Measurement of the current distribution near a substation during a single phase to ground fault

22	S. Bogarra, A.M. Grau, A.L. Orille, Universitat Politècnica de Catalunya (Spain)

##### Surge arrester's location using fuzzy logic techniques

23	J. Montanya, J. Bergas, UPC – EUETIT, B. Hermoso, UPNA (Spain)

Basis for lightning warning systems based in natural electric field measurement

II	CONNECTION OF DISTURBING INSTALLATIONS (EMISSION LIMITS FOR HARMONICS, FLICKER OR UNBALANCE; FILTERS OR COMPENSATORS)

24	R. Grünbaum, M. Noroozian, A. Palesjö, ABB Utilities AB (Sweden)

Connecting the London underground to the public grid : solutions for safeguarding of power quality

25	Z. Hanzelka, A. Bien, W. Loziak, K. Piatek, M. Piekarz, A. Pietrucha, M. Szlosek, University of Mining and Metallurgy, Z. Olczykowski, Radom Technical University, E. Galon, L. Smajek, Institute of Power Engineering, A. Wolski, Electrotechnical Institute (Poland)

##### Comparative tests of flickermeters

26	A. Apostolov, Alstom T&D EAI (U.S.A.)

Web-enabled power quality monitoring in small distribution substations

27	D. Guillot, Alstom T&D (France)

##### Power quality measurement & monitoring

28	Z. Zhang, N.R. Fahmi, Aston University (United Kingdom)

Electric Arc Furnace (EAF) features and its compensation by cascaded multilevel SVG

29	J. Barros, E. Pérez, A. Pigazo, University of Cantabria (Spain)

Real time system for identification of power quality disturbances

30	K. Kahle, CERN - European Organization for Nuclear Research (Switzerland), T. Larsson, ABB Utilities AB (Sweden)

The new 150 Mvar 18 kV Static Var Compensator (SVC) for CERN

31	L. Berthet, D. Boudou, P. Eyrolles, X. Mamo, J. Martinon,  Electricité de France

State of play of the harmonic levels on the French low-voltage networks

32	O. Gonbeau, L. Berthet, D. Boudou, J.-L. Javerzac, Electricité de France

Method to determine contribution of the customer and the power system to the harmonic pollution

33	W. Gawlik, University of Erlangen (Germany)

Optimal placement and mutual influence of active filters

34	M. Scutariu, FDFEE Electrica Muntenia Sud, P. Postolache, C. Toader, University Politehnica Bucharest (Romania)
G. Chicco, R. Napoli, Politecnico di Torino (Italy)

Investigations upon neutral loading in low-voltage distribution networks under harmonic perturbation penetration

35	F. Ferrandis, J. Amantegui, F.J. Pazos, Iberdrola Distribución Eléctrica (Spain)

Power factor correction within industrial sites : Experiences regarding power quality and EMC

36	P. Delarue, P. Bartholomeus, Université des Sciences et Technologies de Lille - L2EP (France) 
E. De Jaeger, F. Minne, Laborelec (Belgium)

Study of harmonic currents introduced by three-phase PWM-converters connected to the grid

37	V.N. Tulsky, I.I. Kartashev, R.G. Shamonov, Moscow Engineering Institute (Russia)

##### Assessing of impact of distrubing load on power quality

38	J. Ghijselen, J. Melkebeek, W. Ryckaert, Ghent University (Belgium)

Distribution system parameters and their influence on harmonic propagation

39	L. Ganyun, G. Lu, H. Cheng, Shanghai Jiaotong University, W. He, G. Pan, J. Zhang, Shanghai Eastern Power Supply Company (China)

Harmonic analysis of the PWM inverter fed linear synchronous motor drive system in the TRANSRAPID Shanghai

40	C. Saniter, R. Hanitsch, D. Schulz, TU Berlin (Germany)

Using small signal frequency domain modelling for predicting harmonic and interharmonic distortions generated by two back-to-back PWM converter

41	A. Bachry, Z. Styczyinski, Otto-von-Guericke-University Magdeburg (Germany)

An investigation of voltage quality in distribution systems with pulsed power loads - Modeling methods verified by synchronous measurements

42	J. Braun, I.S. Burnett, V.J. Gosbell, University of Wollongong (Australia)

##### Description shemes for power quality data

III	VOLTAGE DIPS AND DISTRUBANCES IN CUSTOMERS INSTALLATIONS (IMMUNITY LEVELS, REMEDIAL MEASURES, ETC)

43	I. Attia, K. Youssef, Alexandria Electricity Distribution Company (Egypt)

##### How to secure power quality for sensitive loads

44	A. Lashkar Ara, Azad University of Dezfoul, S.A. Nabavi Niaki, Univeristy ofd Mazandaran (Iran)

Comparison of the FACTS equipment operation in transmission and distribution systems

45	J. Rull, J. Bergas, S. Galceran, CITCEA-UPC, J. Casas, X. Corbella, ENDESA (Spain)

Voltage dips in industrial plants : identification methodology, effects and solutions. Immunization cases.

46	A. Sudria, S. Galceran, CITCEA-UPC, X. Corbella, ENDESA, G. Yeste, ABB (Spain)

Susceptibility of adjustable speed drives in relation to their environment

47	M. Bollen, Chalmers University of Technology (Sweden)

Voltage dips in distribution systems load effects, measurements and theory

48	N. Melo, A. Amorim, EDP Distribução Energia (Portugal)

##### Power quality in industrial customers ?  Case studies

49	E. Tironi, A. Agustoni, M. Brenna, Politecnico di Milano, G. Ubezio, SIEL S.p.A. (Italy)

Proposal for a high quality DC network with distributed generation

50	P. Goossens, A. Robert, ELIA (Belgium)
M. Bollen, Chalmers University (Sweden)

Improved assessment of voltage dips with common monitoring devices

51	R. López García, J.P. Rasgado Casique, Instituto de Investigaciones Electricas (Mexico), S. Galceran, A. Sudrià, Polytechnical University of Catalonia (Spain)

Analysis of new technologies of storage energy for power quality solutions in distribution network

52	F. Zavoda, M. Tremblay, Hydro-Québec – IREQ, G. Simard, Hydro-Québec (Canada)

System originating dips, short interruptions, swells and "Canadian Power Quality Survey 2000"

53	M. Didden, R. Belmans, W. D'Haeseleer, University of Leuven, K. Stockman, PIH Kortrijk (Belgium)

Considerations to choose the appropriate voltage sag mitigation device

54	J. Galarza, S. Aurtenechea, E. Oyarbide, Mondragon Unibertsitatea (Spain)

Selection criterias for single-converter Voltage Sag and Outage Compensator

55	R. Targosz, Polish Cooper Promotion Centre (Poland)
H. De Keulenaer, European Copper Institute (Belgium)

CEBWI - Power quality in non residential buildings - market research in Central Europe

56	T.B. Littler, The Queen's University of Belfast, D.A. Courtney, Ametek Power Instruments, A. Ferguson, SP Power Systems (United Kingdom)

Benchmarking in power quality monitoring to improve equipment resilience to voltage dips

57	M. Häger, STRI AB, R. Mattsson, SSG, A. Sjödin, Elforsk (Sweden)

Reduced PQ-related costs for the Swedish pulp & paper industry

58	A. Jaafar, Z. Tajul Arus, Tenaga Nasional Berhad (Malaysia) 
W. Corbell, Southern California Edison (U.S.A.)

Managing power quality issues through reducing the compatibility gap : a Malaysian experience

59	A. Mäkinen, P. Järventausta, P. Verho, Tampere University of Technology, A. Rinta-Opas, Koillis-Satakunnan Sähkö Oy (Finland)

Comprehensive development of power quality management and evaluation of voltage dip problems

60	J. Mora, D. Llanos, J. Meléndez, University of Girona, S. Corbella, J. Losada, FECSA - Endesa (Spain)

Qualitative representation for cause based classification of sags measured in a distribution substation

61	C. Herath, V. Gosbell, S. Perera, D. Robinson, University of Wollongong (Australia)

##### A transient index for reporting power quality surveys

62	N. Kagan, T.L. Arango, E. Ferrari, N. Matsuo, S.D. Xavier,University of São Paulo, W.B. Santos, CELPE, A. Tenório, AES Eletropaulo (Brazil)

Estimation of short duration voltage variations in medium voltage and subtransmission networks

IV	POWER QUALITY AS SEEN BY THE DIFFERENT PLAYERS IN THE COMPETITIVE MARKET (SYSTEM OPERATOR, REGULATOR, CUSTOMERS)

63	M.V. González Sábato, J. Crudo, ADEERA (Argentina)

Experiences gathered and new regulatory rules related with the quality of service in Argentina

64	Z. Hanzelka, M. Chechelski, R. Jarocha, W. Loziak, M. Rogo, J. Strzalka, M. Wlodarczyk, University of Mining and Metallurgy (Poland)

Measurements of the power quality factors at a coupling point of distribution and transmission systems

65	N. Eassa, A.A. Elseoud, Alexandria Electricity Distribution Company (Egypt)

Assessment of the quality of supply in Alexandria system and economic appraisal of voltage disturbance

66	S. Klinger, DREWAG (Germany)

##### Tailor-made solutions of power supply

67	V. Roberts, A. Colinson, EA Technology (United Kingdom)

Benchmarking the performance of distribution networks

68	H. De Keulenaer, European Copper Institute (Belgium)
R. Targosz, PCPC (Poland)

Status on power quality in low voltage electrical installations in Europe

69	V. Detrich,K. Matonoha, Z. Spacek, EGU Brno a.s. (Czech Republic)

Some new results of reliability analyses carried out in MV distribution networks

70	J.R. Saenz, P. Eguia, E. Fernández, E. Torres, Universidad del País Vasco, F. Jurado, University of Jaen, J. Arceluz, Iberdrola (Spain)

The impact of the new quality of supply regulatory framework in Spain on the network user

71	S. Gheorghe, ELECTRICA Muntenia Sud, S.L. Boghiu, Electrica SA (Romania)

Power Quality - Technical and services performance in Romanian electricity distribution system

72	A. Bordonetti, Azienda Energetica S.p.A. - Etschwerke AG (Italy)

The continuity of electricity supply - Total control : from HV network to LV customer. A software application created by Azienda Energetica S.p.A., in accordance to the Italian normation

73	M. Schwan, Forschungsgemienschaft für elektrische Anlagen und Stromwirtschaft (Germany), W. Friesenecker, A. Kogler, R. Nenning, Vorarlberger Kraftwerke AG (Austria)

Application of an extended outage statistic in the liberalised market

74	G. Beaulieu, Hydro-Québec (Canada) on behalf of CIGRE WG36.07/CIRED

Power quality indices and objectives for MV, HV and EHV systems - CIGRE WG 36.07 / CIRED progress

75	J. Driesen, R. Belmans, Katholieke Universiteit Leuven, G. De Corte, U.I.A., H. De Keulenaer, E.C.I., M. Machiels, U.I.E. (Belgium)

The LEONARDO Power Quality Initiative (LPQI), an integrated approach towards e-learning in electrical engineering

76	M. Dussart, Laborelec (Belgium)

##### Unavailability reduction and its cost

77	P. Van der Sluijs, F. Provoost, NUON TPC (Netherlands)

Results of long term power quality monitoring in the Nuon grid

78	J.A.K. Douglas, F. Castro Sayas, PB Power Ltd. (United Kingdom)

Setting of targets for continuity of supply through benchmarking

79	A. Prudenzi, University of L'Aquila, A. Ardito, S. Malgarotti, CESI S.p.A., R. Lamedica, University of Rome "La Sapienza" (Italy)

A survey  of electricity reliability costs for industrial customers in Italy

80	P.E. Issouribehere, J.C. Barbero, Universidad Nacional de la Plata, G.A. Ingani, J.L. Martinez, L.D. Mazzeo, ENRE (Argentina)

Supply reliability control in the Buenos Aires metropolitan area - Statistical methods results and evaluation

81	V. Gosbell, D. Robinson, University of Wollongong (Australia)

A study of continuous PQ disturbance levels in MV/LV distribution systems

82	S. Lindgren, Vattenfall Sveanat AB (Sweden)
B. O'Sullivan, FMC Tech Limited (Ireland)

A maintenance free monitoring solution for medium voltage overhead networks, to address new demands from the regulator on power quality performance

##### SESSION  3 ("Operation, control and protection")

10	F. Orban, J.-L. Orban, Gillam-Fei s.a. (Belgium)

A practical IT based tool to improve distributor's quality of supply

12	R. Naggar, J. Dallaire, C. Langheit, Hydro-Québec (Canada)

FIORD - Knowledge engineering for the evaluation of voltage continuity

35	R. Cerero, M. Abendaño, A. González, Iberdrola Distribución Eléctrica (Spain)

Integration of control centre and power quality information at Iberdrola

##### SESSION 4 ("Dispersed generation")

28	D. Schulz, R. Hanitsch, C. Saniter, TU Berlin (Germany)

Power quality behaviour of powerful wind parks with variable speed wind energy converter

39	T. Degner, A. Engler, M. Viotto, ISET e.V. (Germany)

Effect of renewable energy sources on power quality - Recent research activities

59	B. Buchholz, C. Boese, Siemens AG, N. Lewald, Stadtwerke Karlsruhe GmbH (Germany)

Power quality improvement through generation and power exchange on distribution level

SESSION 6 ("Management – Organisation – Skills")

7	A. Friday, ERA Technology Ltd., C. Watts, Ofgem, G. Stott, British Power International, I. Boira Segarra, Mott MacDonald (United Kingdom)

Improving quality of service information and incentives in the UK electricity distribution industry

22	P. Byrne, R. Koch, D. Pillay, Eskom Distribution (South Africa)

The value of power quality customer forums in a regulated environment

26	P. Birkner, Lech-Elektrizitätswerke AG (Germany)

Guaranty of supply availability in a competitive environment - Strategy and experience of a german distribution company

31	K. Samdal, G. Kjolle, SINTEF Energy Research, B. Singh, Institute for Research in Economics and Business Administration, F. Trengereid, The Norwegian Water Resources and Energy Directorate (Norway)

##### Customers interruption costs - what's the problem ?

42	A. Arcos Vargas, J. González Lara, J. Frau Valentí, ENDESA Distribución Eléctrica (Spain)

Quality economy level in a competitive market. Electricity's company vision

54	S. Reid, Stone and Webster Consultants, S. Curcic, Power Technologies International Ltd. (United Kingdom)

Comparison of distribution business' service performance - a performance based regulation

# Footnotes

In the following we will use the american terminology “ground” and “grounding” as equivalent to “earth” and “earthing”

Paper 6.54 states that the chosen quality indices are CIs – the number of customer interruptions per 100 connected customers (annual average) and CMLs – the number of customer minutes lost per connected customer (annual average).

Change rate : 1 EUR = 7.9 NOK (31/03/2003).

# Comments

Deleted since you are introducing this later