## Slide 1: The Location of Switchgear Partial Discharge by Panel and Techniques to Correlate Switchgear and Cable Partial Discharge with Load and Substation Environment Cliff Walton and Sarah Carter - PPA Energy Colin Smith - IPEC Matthieu Michel - UK Power Networks
Cliff Walton – UK – Session 1 Network Components – 0862

## Slide 2: Introduction
UK Power Networks on line monitoring switchgear and cable partial discharge updates:
  Early warning of potential switchgear failure
  Understanding of effect of substation environment on switchgear partial discharge
  Relationship between switchgear and cable partial discharge and load and techniques for enhanced criticality measurement
Cliff Walton – UK – Session 1 Network Components – 0862

## Slide 3: 63 substation sites monitored > 1000 feeders > 2200 sensors HF CTs Capacitive couplers Ultrasonic 5-10 years of data 6.6kV-225kV

## Slide 4: Switchgear pd and precedence detection
Switchgear pd signal spreads along busbar
Can be detected on multiple panels
Panel in South of England, single source of activity P14
Cliff Walton – UK – Session 1 Network Components – 0862
Notes: Air insulated switchgear,
PD induces transient voltages which propagate rapidly over metal panels
High frequency , skin effect, move to adjacent panels
PD magnitude generally diminishes with distance
Complex \RF energy dissipation, amplitude is unreliable way of determining source
Further complicated when more than one source

## Slide 5: Precedence solution
Precedence unit
Corrects for signal cable lengths
Detects which channel was first to see pd signal
Eliminates signals which are not precedent
Trials in 10 substations show accurate to within 400 mm
Cliff Walton – UK – Session 1 Network Components – 0862

## Slide 6: Precedence solution
PD in site with two pd sources
Before precedence:
After precedence:
2 discharging panels – P14 and P5 confirmed
Cliff Walton – UK – Session 1 Network Components – 0862

## Slide 7: Examples of switchgear discharges

## Slide 8: Switchgear pd and the environment
Indoor substations equipped with temperature and humidity sensors
Weather station installed externally
Cliff Walton – UK – Session 1 Network Components – 0862
Substation in southwest London

## Slide 9: Switchgear pd and the environment
Observed strong interrelationships between temperature, humidity and switchgear type
Large number of discharges at higher temperature can have lower energy
Cliff Walton – UK – Session 1 Network Components – 0862
PD Activity
PD Energy
Count

## Slide 10: Switchgear pd and the environment
Environmental dependency determined
No
Yes
Load
Temperature
Humidity
Pressure
Model
PD
Historic pd data and switchgear type – used to establish boundaries within model
Predict occurrences of PD
Actively control substation environment
Reduce pd, improve switchgear health and life
Cliff Walton – UK – Session 1 Network Components – 0862
96% correlation

## Slide 11: The relationship between pd and load
Cable and switchgear PD associated with load profiles
In some instances failures follow and load increase or decrease
(a) On the falling edge (cooling)
(b) At a minimum
(c) On the rising edge (heating)
Or Independent of load.
A Key input into assessment of Event Criticality
Cliff Walton – UK – Session 1 Network Components – 0862
Notes: On falling edge – transition 1
On rising edge – transition 2
At a minimum – transition 3
Continuous and independent of load

## Slide 12: The relationship between pd and load
Cliff Walton – UK – Session 1 Network Components – 0862
Online event location

## Slide 13: Evolution of pd and load hysteresis
Cliff Walton – UK – Session 1 Network Components – 0862
Higher likelihood of failure

## Slide 14: The relationship between pd and load
Measures of hysteresis
  Shape – Aspect Ratio
  Area
  Position Displacement
Cliff Walton – UK – Session 1 Network Components – 0862
July
2009
January
2010
Monitor evolution of incipient fault
Knowledge of load dependency – operational considerations

## Slide 15: Conclusions
Precedence detection remotely locates discharging switchgear panels to within 400mm
Active control of substation environment to prevent discharge and improve asset health
PD and load relationship indicators determined to enhance assessment of event criticality
Cliff Walton – UK – Session 1 Network Components – 0862