## Slide 1
In France, LV customers are mostly < 18 kVA and single-phase.
Some LV networks are unbalanced and it generates important voltage drops
It is not a problem in urban zone
  bulking effect
But a real problem in rural zone
  long LV network and few customers
So far usual solutions are network reinforcement
Yves ZONTA & Christophe GAUDIN – France – S1 – 0170
Unbalanced rural LV networks in France

## Slide 2
4 equipments are developed to compensate the unbalance currents effects
  Two old systems : from the early 2000s.
  Two new systems : quite recently
The firsts are efficient but heavy and expensive
  VAS (Voltage Adapter Slipper) and TMC (Tri-Mono Converter)
The new ones are thinner and less expensive (/3)
  BMC (Bi-Mono Converter) and TNB (Three-phase Network Balancer)
Yves ZONTA & Christophe GAUDIN – France – S1 – 0170
An alternative to reinforcement

## Slide 3: Voltage Adapter Slipper (VAS)
Electronic control load regulator : maintains the output voltage within the range of 230V +10/-10%.
Capacity of the equipment :
  1 single-phase customer up to 18 kVA
Cost : 15 to 25 k€ (including installation)
    Weight : 200 to 450 kg
    for single & three phase systems
Ph
N
Switches
Switched transformer
Network
Customer
Serial
transformer
Single Phase VAS
Electrical service connection
Customer
Yves ZONTA & Christophe GAUDIN – France – S1 – 0170

## Slide 4: Tri/Mono Converter (TMC)
Allows the network to see the customer as a three-phase well-balanced customer
Capacity of the equipment :
  1 single-phase customer up to 12 kVA
Cost : around 10 k€ (including installation)
    Weight : 250 kg.
Yves ZONTA & Christophe GAUDIN – France – S1 – 0170
N
Ph1
Ph2
Ph3
Network
Customer
N
Ph
TMC
Customer
Network

## Slide 5: Bi/Mono Converter (BMC)
Allows to distribute the power of the single-phase customer on two phases
Capacity of the equipment :
  1 single-phase customer up to 9 kVA
Cost : only 5 k€ (including installation)
    Weight : only 70 kg
Yves ZONTA & Christophe GAUDIN – France – S1 – 0170
Customer
N
Ph1
Ph2
Ph3
Network
N
Ph
400 / 230
BMC
Customer
Network

## Slide 6: Three-phase Network Balancer (TNB)
A coupling ZIGZAG creates a neutral point & rebalances the network with a current circulation in the resistor Zn & neutral
Capacity of the equipment :
  Single-phase and three-phase customers up to 45 A on each phase.
Cost : only 5 k€ (including installation)
    Weight : only 70 kg
Yves ZONTA & Christophe GAUDIN – France – S1 – 0170
Ph1
Zn
Ph2
N
Ph3
I ≤ 40A
TNB
Network

## Slide 7
Yves ZONTA & Christophe GAUDIN – France – S1 – 0170
C H A R A C T E R I S T I C S | Materials | Voltage drop corrections | Capacity | Weight | Cost | 
 | Three-phase VAS | till 20 % | 12 kVA /phase | 400 kg | 25 k€ | 
 | Single-phase VAS | till 20 % | 18 kVA | 220 kg | 15 k€ | 
 | TMC | / 6 | 12 kVA | 250 kg | 10 k€ | 
 | BMC | /3 | 9 kVA | 70 kg | 5 k€ | 
 | TNB | / 2 | up to 45 A /phase. | 70 kg | 5 k€ | 

## Slide 8
Economic conditions
  Network should last at least 10 years
  No new customer expected or load increase
  Should cost half of network reinforcement (best capitalized cost approach)
Electric conditions
  Possible difficulties in case of upstream customers
  Need of tool for electric calculation (unbalanced network)
Conclusion : a good solution for long LV networks with few customers but there are the above limitations to consider
Yves ZONTA & Christophe GAUDIN – France – S1 – 0170
Some Points to take into account