## Slide 1: Impacts of Inductive and Conductive Interference due to High-Voltage Lines on Coating Holidays of Isolated Metallic Pipelines
René Braunstein

## Slide 2
René Braunstein– AT – S2 PQ&EMC – 0013
Introduction
A.C. voltage interference
  Capacitive Interference
  Inductive Interference
  Conductive Interference

## Slide 3
René Braunstein– AT – S2 PQ&EMC – 0013
Coating Holidays?
Small defects of isolating pipeline coating
Coating Holidays + Inductive and/or conductive Interference  
Material removal

## Slide 4
René Braunstein– AT – S2 PQ&EMC – 0013
A.C. corrosion likelihood
CEN/TS 15280 - Comité Européen de Normalisation
Normal operation – long-term influence
a.c. voltage should not exceed: RMS a.c. current density (J ~) :
10 V für RE > 25 Ωm; J ~ < 30 A/m2: no/low likelihood
4 V für RE < 25 Ω J ~ 30 A/m2 - 100 A/m2 : medium likelihood
at any time J ~ > 100 A/m2 : very high likelihood

## Slide 5
René Braunstein– AT – S2 PQ&EMC – 0013
Modelling Coating Holidays (1)
1 … R leakage in the soil
2 … R pore
3 … R polarisation
4 … Coating
5 … Steel
d … pore diameter
t … depth of the pore
(coating thickness)
Source: CEN/TS 15280: Evaluation of a.c. corrosion likelihood of buried pipelines- Application to cathodically protected pipelines. CEN, March 2006, modified.

## Slide 6
René Braunstein– AT – S2 PQ&EMC – 0013
Modelling Coating Holidays (2)
Simplified as a circular plate earthing system
Source: CEN/TS 15280: Evaluation of a.c. corrosion likelihood of buried pipelines- Application to cathodically protected pipelines. CEN, March 2006, modified.
ρE … Specific soil resistivity in Ωm
d … Coating holiday diameter H … Distance between earth‘s surface and Coating Holiday

## Slide 7
René Braunstein– AT – S2 PQ&EMC – 0013
Dependency on specific soil resistivity ρE
d= 1 mm
d= 5 cm

## Slide 8
René Braunstein– AT – S2 PQ&EMC – 0013
Currents over Coating Holidays
d= 1 mm
d= 5 cm

## Slide 9
René Braunstein– AT – S2 PQ&EMC – 0013
Current Densities at Coating Holidays
d= 1 mm
d= 5 cm

## Slide 10
René Braunstein– AT – S2 PQ&EMC – 0013
Conductive Interference (1)
Pi – equivalent circuit of influenced pipeline segments

## Slide 11
René Braunstein– AT – S2 PQ&EMC – 0013
Conductive Interference (2)

## Slide 12: Summary
Coating Holidays can bee seen as very high impedant earthing systems
A.C. corrosion likelihood decreases with raising ρE
The cumulated impact of inductive and conductive interference is relevant for A.C. corrosion
The shown values can be seen as practicable reference values
René Braunstein– AT – S2 PQ&EMC – 0013