## Slide 1
MUKKA – SE – Session 2 – 0552
Dynamic var compensation of mine hoists for improvement of power quality and increase of productivity at LKAB Sweden
Lennart Mukka | Natan Gothelf | Christian Payerl
LKAB Sweden | Harmonizer PQC Sweden | ABB Sweden
Authors:

## Slide 2
Introduction
Function
Design features
Results of Performance Tests
Operating experience
MUKKA – SE – Session 2 – 0552
Content

## Slide 3
MUKKA – SE – Session 2 – 0552
Luossavaara Kiirunavaara AB
LKAB
LKAB is the largest producer of iron ore products in EU
Annual production last year was 26 million tonnes
The customers are steelworks in Sweden, Europe, Far East and Middle East

## Slide 4
MUKKA – SE – Session 2 – 0552
Kiruna

## Slide 5
MUKKA – SE – Session 2 – 0552
Network model

## Slide 6
MUKKA – SE – Session 2 – 0552
Hoist motors

## Slide 7: Load characteristics Reactive Power per phase
MUKKA – SE – Session 2 – 0552

## Slide 8: Load characteristics Active Power per phase
MUKKA – SE – Session 2 – 0552

## Slide 9: Limitations of the hoisting system
Large voltage variations and high harmonic distortion enforcing start of only one hoist motor at a time

## Slide 10
Increase of production capacity by enabling simultanous start of 4 motors
Reduction of voltage variations
Reduction of harmonic distortion
MUKKA – SE – Session 2 – 0552
Purpose of the SVC installation

## Slide 11
MUKKA – SE – Session 2 – 0552
Selected SVC solution

## Slide 12
MUKKA – SE – Session 2 – 0552
Selected SVC solution

## Slide 13: Special design considerations
Effect of long cables on filter tuning
Effects of temperature range –50/+40deg.C
Selection of air clearances and creepage distances with regard to ice, snow and air pollution

## Slide 14: Performance tests
Flicker
Voltage variations
Active power, Reactive power, Power factor
Harmonic voltage distortion
Transformer Fundamental- and Harmonic currents
Filter Fundamental- and Harmonic currents
Measurements of:

## Slide 15: Performance tests’ results
Active Power
Reactive Power
Voltage variations
Harmonic distortion

## Slide 16: Performance tests summary (1)
Parameter
Limit
Result
Flicker
1,0
0,9
Max. voltage variations
3%
3%
Power factor
0,98
0,998
Voltage distortion UTHD
4,8%
3,2%
Individual voltage distortion, odd harmonics
<60% of compatibility limits acc. to EN 50160
< Limit
Individual voltage distortion, even harmonics
<60% of compatibility limits acc. to EN 50160
< Limit
Total current distortion ITHD
5%
2%
Individual current distortion
3%
≤ 1,6 %
6 kV bus bar

## Slide 17: Performance tests summary (2)
Parameter
Limit
Result
Flicker
1,0
0,3
Max. voltage variations
3%
1,3%
Power factor
n.a
n.a.
Voltage distortion UTHD
1,5%
0,84%
Individual voltage distortion, odd harmonics
1,0%
0,75%
Individual voltage distortion, even harmonics
0,2%
0,05%
Total current distortion ITHD
5%
2%
Individual current distortion
3%
≤ 1,6 %
145 kV bus bar

## Slide 18: Conclusions from the performance tests
The results of the verification measurements have proved that all performance requirements have been met or exceeded. It has been also verified that the ratings of the SVC and SVC components are correctly selected in order to withstand the fundamental- and harmonic load during the most severe operation conditions.

## Slide 19: Operation experience
Voltage variations without SVC
due to 29 MW hoist load
Voltage variations with SVC
due to 33 MW hoist load
Result: 30% increase of hoist capacity

## Slide 20: Thank you for your attention