## Slide 1: FLEXIBLE THERMAL LOAD MANAGEMENT FOR ANCILLARY SERVICES MARKET: EXPERIENCE OF SWISS SMART GRID PILOT PROJECT
Elvira Kaegi1 Daniel Berner2 Adrian Peter2
1 Neo Technologies SA – Switzerland
2 BKW FMB Energie AG – Switzerland
Elvira Kaegi – Switzerland – Session 4 – Paper 0481

## Slide 2: Smart Grid Pilot-Project iSMART
Project-Leader: BKW
Regional Power Supply Company of Cantons Bern and Jura, Switzerland.
Participants:
200 residential customers.
Time-horizon:
2010-2012.

## Slide 3: Product FLEX: loads provide ancillary services
Scope:
flexible dispatch of thermal loads (water heaters, heatings, heat pumps) in order to provide tertiary control on demand of ISO (Swissgrid)
Elvira Kaegi – Switzerland – Session 4 – Paper 0481

## Slide 4: Participation in Swiss Tertiary Reserve Market
Qualification criteria for Pool- Tertiary Reserve Provider of Swissgrid:
Minimal power: ±1MW
Bid blocks: 6 fixe blocks of 4 hours
(0:00 – 4:00 – 12:00 – 16:00 - 20:00 – 24:00)
Request: anytime during a bid block (per mail/phone)
Duration: on request till the end of the block
Potential BKW:
Power drawn by water heaters 140 MW x 8 h=1120 MWh Now: fixed time-frame ripple control group switching
Flexible use allows for 1120 MWh/24h= 47 MW / hour
Elvira Kaegi – Switzerland – Session 4 – Paper 0481

## Slide 5: Smart Grid Approach to Thermal Appliances Management
Pilot installation conditions:
No change in existing internal appliance controlling (thermostat-controlled Water Heater operation)
No temperature measurements
Low tariff forced for commutations during the HT time periods
For 50 Pilot domestic Water Heaters:
50 x 5kW = 250 kW
Practical availability assumption: about 10-100 kW
State Estimation-Based Control
Elvira Kaegi – Switzerland – Session 4 – Paper 0481

## Slide 6: Water heater Load Control Principle
The heating / cooling cycle duration of Water Heater is modified resulting in different Tertiary Reserve Potential
Elvira Kaegi – Switzerland – Session 4 – Paper 0481

## Slide 7: Definition of Tertiary Reserve Potential
Tertiary Reserve Potential is defined as forced power consumption reduction or increase during requested time interval without comfort reduction of the appliance owner (residential water heater user)
This potential depends on:
      Water-Heater Hysteresys: Tmin ON ≤ T(t) ≤ T OFF
      Definition of minimal water temperature Tmin
      Individual hot water usage patterns
Learning phase required
Elvira Kaegi – Switzerland – Session 4 – Paper 0481

## Slide 8: Water heater load control algorithm
Bidding in the TR Auction
YES
NO
Follow actual dispatch
START, t=0
END, t=96
End-Temperature Estimation T(t=96)
tSTART ≤ t ≤ tEND
YES
NO
t<96
Send control signals according to the ranking table
(„first in – first out“ principle)
Any TR Request ?
Combine Water Heater Groups
Boiler-Dispatch Update
Measure actual power
For t=[t : t+16] : calculate max TR-Potenzial
TR-Potential Calculation for 96 Intervals (15min samples)
Boiler-Ranking calculation

## Slide 9: Tank temperature estimation for water heater dispatch
T,°C
0 2 4 6 8 10 12 14 16 18 20 22 24
Tmax OFF=60°
Tmin ON=55°
T (t)
Tmin =45°
Standby
Heating Cycle=50 min
Heating Cycle=15 min
Heating Cycle
Standby
Hot Water Usage
Hot Water Usage
Thermal Losses (Standby)
Elvira Kaegi – Switzerland – Session 4 – Paper 0481

## Slide 10: Tank temperature estimation for water heater dispatch
T,°C
Tmax OFF=60°
Tmin ON=55°
T (t)
Tmin =45°
Standby
Heating Cycle
Standby
Hot Water Usage
Thermal Losses (Standby)
0 2 4 6 8 10 12 14 16 18 20 22 24
Possible TR bid blocks
Hot Water Usage
Elvira Kaegi – Switzerland – Session 4 – Paper 0481

## Slide 11: Example: Water Heater 300l, 6kW TR-Bid Block 10:00-11:00 a.m.
0 2 4 6 8 10 12 14 16 18 20 22 24
Standby
kTL= -0.33°C/h
TENDE >=45°C
kHWU= - 12 °C/ St.
Standby
kTL= -0.33°C/h
TR Bid
tMax HC= 52 min
TSTART >=55°C
kHWU = - 12 °C/ St
Standby
kTL= - 0.33°C/h
TEND=60°C
T START = 45°C
Last Value Day d-1
No TR Request
T,°C
Tmax OFF=60°
Tmin ON=55°
T (t)
Tmin =45°
TR Request
Heating Cycle
kHC =17°C/St

## Slide 12: Current State of the Implementation
Water Heater tank temperature estimator implemented (Matlab-Simulink)
Interface for manual version of dispatch programs implemented and successfully tested
Water Heater control substituted for FLEX at Pilot Customers’ locations
Algorithm implementation under contruction
Planned full version introduction: Fall 2011
Results evaluation: Fall 2012
Elvira Kaegi – Switzerland – Session 4 – Paper 0481

## Slide 13: Thank you for your attention!
Elvira Kaegi – Switzerland – Session 4 – Paper 0481