## Slide 1: FIELD TEST OF GRID ORIENTED MICRO CHP UNITS FOR DOMESTIC ENERGY SUPPLY
Dipl.- Wirtsch. Ing. Arne Dammasch
Prof. Dr.-Ing. Michael Kurrat

## Slide 2
phase 1:
conception and development of a schedule planning algorithm for a grid oriented operation mode of micro CHP units
phase 2:
computer-based simulation of a virtual power plant consisting of micro CHP units is implemented
test starts on the micro CHP unit at the TU Braunschweig and further improvements of the control interface are accomplished
phase 3: (since January 2011)
testing and validation of simulation results within a field trial
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Project phases

## Slide 3
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Grid oriented operation mode of micro CHP units
electrical load
time
grid load without CHP
grid load with CHP
Notes: A smoothening of the grid load can be achieved by operating the CHP units grid oriented.
The operation times are mostly in peak load times of the electrical grid.

## Slide 4
phase 1:
conception and development of a schedule planning algorithm for a grid oriented operation mode of micro CHP units
phase 2:
computer-based simulation of a virtual power plant consisting of micro CHP units is implemented
test starts on the micro CHP unit at the TU Braunschweig and further improvements of the control interface are accomplished
phase 3: (since January 2011)
testing and validation of simulation results within a field trial
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Project phases

## Slide 5
simulated settlement with 30 micro CHP units and 100 house connections
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Simulation results
1 micro CHP unit
2 micro CHP units
5 micro CHP units
10 micro CHP units
15 micro CHP units
20 micro CHP units
25 micro CHP units
30 micro CHP units
electrical load in kW
time in ¼ h
resulting residential load
original residential load

## Slide 6
phase 1:
conception and development of a schedule planning algorithm for a grid oriented operation mode of micro CHP units
phase 2:
computer-based simulation of a virtual power plant consisting of micro CHP units is implemented
test starts on the micro CHP unit at the TU Braunschweig and further improvements of the control interface are accomplished
phase 3: (since January 2011)
testing and validation of simulation results within a field trial
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Project phases

## Slide 7
two apartment buildings in Braunschweig /Germany , each is equipped with a micro CHP unit
micro CHP unit: EcoPower e4.7 (4.7 kWel / 12.5 kWth )
thermal storage tank (1,000 liter)
existing boiler remains as a peak load boiler
measurement and control system:
central schedule management
data aquisition for one building: 18 temperature sensors 4 fluid-flow meters 1 control unit per micro CHP unit 1 UMTS-Router
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Information about the field test
daily amount of logged data for one building: 198,720 measured values!

## Slide 8
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Installation and start of the field test
Braunschweig
11/23/2010
and
01/04/2011
peak load boiler
micro CHP unit
thermal storage tank

## Slide 9
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Structure of the heating-system
thermal storage
peak load boiler
micro CHP unit
heating circut
hot water
measurement hardware
control unit
fluid-flow meter temperature sensor data interconnection heating supply heating return

## Slide 10
each micro CHP unit is equipped with an UMTS-router
fixed IP-address
secure VPN-connection
centralized schedule management
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Information infrastructure
VPN Area
VPN DSL/LAN
VPN UMTS
VPN UMTS
VPN UMTS
centralized schedule management

## Slide 11
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Thermal load and temperature in February 2011
time
time
temperature
in °C
thermal load
in kW

## Slide 12
the measurement system acquires data with high resolution quality
measurement intervall = 10 seconds
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Thermal load and hot water load for February 8, 2011
thermal load
in kW
thermal load
in kW
time
time
thermal load
hot water load

## Slide 13
forecast of thermal and grid load
based on historically data
generation of a day-ahead-schedule for each micro CHP unit of
the virtual power plant
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Load forecast and schedule management
Chart: Zeit [hh.mm]
Chart: 
Chart: 
load in kW
time in hh:mm
scheduled feed-in of the micro CHP unit (February 4, 2011)
grid load (February 2, 2011)
thermal load (February 2, 2011)

## Slide 14
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Quality of the load forecast
Chart: thermal load
Chart: grid load
thermal load (February 2, 2011)
thermal load (February 4, 2011)
load forecast is not one hundred percent accurate
grid load (February 2, 2011)
grid load (February 4, 2011)

## Slide 15
despite less accuracy in the
load forecast…
results only in minor deviations
from the schedule
results:
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Quality of the schedule
Chart: time in hh:mm
Chart: 
Chart: 
Chart: 
DPd | -11.22%
Dsd | -8.47%
DPd: change of peak load Dsd: change of peak spread
real feed-in of the micro CHP unit real grid load without CHP
real grid load with CHP
initial CHP schedule

## Slide 16
grid oriented operation mode can be realized
load forecast directly effects the quality of the operation schedule
optimization of the schedule generation algorithm
development of better load forecasting systems
integration of electrical storage systems
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Conclusion
Outlook

## Slide 17
Dipl.-Wirtsch.-Ing. Arne Dammasch
Working Group Energy Systems
Technische Universität Braunschweig
Institute for High Voltage Technology and Electrical Power Systems – elenia
Schleinitzstraße 23 | 38106 Braunschweig | Germany
Email: a.dammasch@tu-braunschweig.de
Arne Dammasch – Germany – Main Session 4 – Paper 1080
Thank you!