## Slide 1
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
FAULT LIMITING TECHNOLOGIES IN DISTRIBUTION NETWORKS
David KLAUS, Adrian WILSON - Applied Superconductor Ltd, UK; Joachim BOCK, Achim HOBL - Nexans SuperConductors, DE; Darren JONES - Electricity North West, UK; Jamie McWILLIAM – ScottishPower, UK; Alan CREIGHTON CE Electric UK, UK;
Larry MASUR, Franco MORICONI - Zenergy Power plc, UK

## Slide 2
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
Collaboration Agreement for 1 pilot installation each with ScottishPower, Electricity North West and
CE Electric UK

## Slide 3
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
Applied Superconductor’s Role
Understand Network Operator’s Problems
Secure Order and Prepare Specification
Undertake Network Response Studies
Define Routine and Type Test Requirements
Design and Assemble Protection, Control, Monitoring
and Cooling Systems for Pilots 1&2
Deliver, Install, Commission, Monitor and Maintain

## Slide 4
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
Pilot 1 - Electricity North West
11kV resistive SFCL
Normal current 100A
Prospective Fault 20kA rms; 50kA pk
86% clamping
09 2008 Type Tested
03 2009 Installed at site
04 2010 Trial Complete

## Slide 5
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
Pilot 2 – Scottish Power
11kV resistive SFCL
Normal current 400A
Prospective Fault 20kA rms; 50kA pk
85% clamping
12 2010 Type Tested

## Slide 6
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
Pilot 3 – CE Electric UK
11kV pre-saturated core SFCL
Normal current 1250A
Prospective Fault 6.2kA rms; 17kA pk
20% clamping
06 2011 Type Testing in progress

## Slide 7
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
Pilot 4 – CE Electric UK
33kV pre-saturated core SFCL
Normal current 800A
Prospective Fault 8.5kA rms; 23kA pk
40% clamping
06 2011 Design in progress

## Slide 8
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
Pilot 1 - Electricity North West
11kV resistive SFCL
Normal current 100A
Prospective Fault 20kA rms; 50kA pk
86% clamping
09 2008 Type Tested
03 2009 Installed at site
04 2010 Trial Complete

## Slide 9
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 10
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 11
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
48 of the BSCCO components connected in series constitute each phase of the limiter. The series assemblies are immersed in liquid nitrogen cooled to below its boiling point. The nitrogen head pressure is below atmospheric pressure.

## Slide 12
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
fault current
limited fault current
Up to 90% clamping
Clamps within 1.5 ms
Normal current  800A
Recovery within 3 mins
Removes DC component
Resistive Fault Current Limiter

## Slide 13
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 14
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 15
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
Interlocking
Alarms
Temperature Control
Text Reports
SCADA Interface
Remote Control / Monitoring
Data Storage and display
Platform for Relay, PLC programming tools.
P
T1
T2
L1
L2
L3
Helium Compressor
Water Chiller
Programmable
Logic Controller
T3
T4
I 1,2,3
T in
Va
Vb
PC
3G Modem
Internet
Coldhead
T out
H in
Fault Recorder
Protection Relays
Flow

## Slide 16
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 17
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
Successful trial with good availability of limiter
Noise primarily from cooling system requires mitigation
Cryocooler compressor requires cooling water and ambient air temperatures to be maintained within a narrow range
Liquid nitrogen handling straightforward and safe with appropriate training
Limiter impedance has negligible effect on current sharing
Means for remote reset of modems and PC required

## Slide 18
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
Pilot 2 – Scottish Power
11kV resistive SFCL
Normal current 400A
Prospective Fault 20kA rms; 50kA pk
85% clamping
12 2010 Type Tested

## Slide 19
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 20
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 21
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 22
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 23
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 24
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 25
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 26
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
Pilot 3 – CE Electric UK
11kV pre-saturated core SFCL
Normal current 1250A
Prospective Fault 6.2kA rms; 17kA pk
20% clamping
06 2011 Type Testing in progress

## Slide 27
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 28
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 29
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
Pre-saturated Core Fault Current Limiter
fault current
limited fault current
Up to 50% clamping
Instantaneous Recovery
Normal current 2000A

## Slide 30
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 31
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 32
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 33
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 34
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 35
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 36
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 37
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
Pilot 4 – CE Electric UK
33kV pre-saturated core SFCL
Normal current 800A
Prospective Fault 8.5kA rms; 23kA pk
40% clamping
06 2011 Design in progress

## Slide 38
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456

## Slide 39
Thank You!
Klaus D.W. et al. – United Kingdom – RIF Session 1 – 0456
FAULT LIMITING TECHNOLOGIES IN DISTRIBUTION NETWORKS
David KLAUS, Adrian WILSON - Applied Superconductor Ltd, UK; Joachim BOCK, Achim HOBL - Nexans SuperConductors, DE; Darren JONES - Electricity North West,UK; Jamie McWILLIAM – ScottishPower, UK; Alan CREIGHTON CE Electric UK, UK;
Larry MASUR, Franco MORICONI - Zenergy Power plc, UK