## Slide 1: Saturated-Core Fault Current Limiter Field Experience at a Distribution Substation
Franco Moriconi, Francisco De La Rosa, Albert Nelson, Larry Masur, Zenergy Power Inc., US; Detlev Kirsten, Zenergy Power GmbH, DE
CIRED
Frankfurt (Germany)
6-9 June 2011
RIFS1, 0680

## Slide 2
Zenergy Power
FCL Operating Principle and Advantages
FCL Program Overview and Roadmap
Field Experience at Distribution Substation
The Compact FCL design for HV applications
Summary & Conclusions
Outline

## Slide 3: Zenergy’s Business Fields and Markets
Magnetic Billet Heater
(‘MBH’)
Fault Current
Limiter
(‘FCL’)
Industrial
Heating
of Metals
Smart Grid
Hardware
Low-cost large-scale Renewable Energy Generation
In-house coiling
of superconductor
wire
Expertise in superconductive materials
Expertise in products and services
End markets
Next generation
low cost wire (2G)
Coils
for Generators
Image Courtesy of Converteam

## Slide 4: Inherently fail safe and self healing devices for electric utilities
G
Fault Current Limiter
Embedded
Generation
Incoming
Feeder
Bus Tie
Faulty network
Typical applications of Fault Current Limiters:
Network reinforcement
Protection of network components (transformers, switchgear, busbars)
Distributed Generation connection
Power quality
Grid Protection with Fault Current Limiters

## Slide 5: Operating Principle of Saturated-Core FCL Trade Name “Magnetic Fault Current Limiter” (MFCL)
Picture-Frame Iron Cores
AC Coil
AC Coil
Boost
Buck
Configuration for single phase MFCL.
Boost
Buck

## Slide 6: Operating Principle of MFCL

## Slide 7: Advantages
– Fast: acts within the first ¼ cycle
– Self-triggering: passive device
– Self-recovering: does not interrupt current
– Scalable: MV to HV applications
– Robust: designed for 3s short circuit currents
and CB automatic reclosing
– Reliable: 24/7 operation
– Fail Safe: fails in high impedance state ensuring protection at all times
– Automatic: full remote monitoring/data
– Transparent: reduce or eliminate issues associated with reactors. This includes transient recovery voltages and high insertion impedances.

## Slide 8: Zenergy Power Milestones of „Magnetic Fault Current Limiter“ Development
2007
2008
2009
2010
2011
2012
MV lab-scale demonstrator built and tested
12kV prototype built & tested
12kV prototype installed & on the grid from 03.2009 to 11.2010
15kV compact design demonstrators #1,2,3&4 built and tested
11kV commercial prototype built
138kV lab-scale prototypes tested
11kV commercial prototype high power tested
138 kV prototype manufacturing phase #1
33kV commercial design started Q2 2011
11kV commercial prototype landmark operation
138kV prototype three-phase #2&3
138kV prototype landmark operation
2013
2014
2015
HV Prototype
10-36kV com
MV Prototype
Demonstrator
Lab-Test

## Slide 9: - Serving 1400 commercial and residential customers - Online March 9, 2009, collecting data continuously since installation - Scheduled decommissioning in November 2010
Zenergy Power
MFCL
MFCL 15kV Class at SCE Shandin Substation,
San Bernardino, California
Experience at Distribution Substation

## Slide 10
115 kV LINE
115/12kV
Transformer
AUTO-BYPASS
SWITCH
First installation in U.S. electricity grid
Operated by Southern California Edison
Supported by U.S. Department of Energy and California Energy Commission
Experience at Distribution Substation
Notes: 10

## Slide 11
Experience at Distribution Substation
Notes: 11

## Slide 12
Recovery Under Load
23 kA rms X/R=44
3-phase to Ground
30 Cycles
Double Fault
Recovery Under Load
20 kA rms X/R = 22
3-phase to Ground
20 Cycles
Endurance Test
20 kA rms X/R=22
3-phase to Ground
82 Cycles
Fully Tested
Notes: 12

## Slide 13
three seconds phase-to phase fault
Experience at Distribution Substation:
In-grid fault events

## Slide 14: Summary of Operating Experience: MFCL at Southern California Edison´s Shandin substation
MFCL has operated continuously since Mar 2009 and was decommissioned in Dec 2010
Operating in a hot, windy, and dusty outdoor environment (-1°C to +42°C)
Experienced one loss of DC Bias with consequent “resonance” condition (see IEEE paper)
Successful integration with automatic bypass switch by utility
Experienced one fault event with multiple faults in quick succession on 14 January 2010
Rode through two “Loss of Station Power” events
    Effective bypass of MFCL and shut-down of the HTS coil (as expected)
    “Station power failures” caused by grid disturbances not on Avanti circuit
    Instantaneous bypassing sought by SCE
Performed routine maintenance on cryogenics compressors

## Slide 15
AC input
AC output
Picture frame single phase
Compact single phase
HTS coil
Compact MFCL Design

## Slide 16
Compact MFCL – Fully Tested

## Slide 17: Path from DEMONSTRATOR to COMMERCIAL DESIGN
SPIDER:
2.5x2.5 m footprint
Effective core 300 cm2
Rectangular COMPACT:
2.0x1.3 m footprint
Effective core 860 cm2
ROUND COMPACT:
1.8m OD footprint
Effective core 750 cm2
FROM
DEMONSTRATOR
TO
PROTOTYPE
TO
COMMERCIAL PRODUCT

## Slide 18: MFCL System for CE Electric substation, UK
Customer: ASL
Operator: CE Electric, UK
15 kV Voltage Rating
3-Phase, 50 Hz
1.25 kA Nominal Current
17 kApeak Prospective Fault Current
3 Second Fault Duration
<1% Insertion Impedance
Reduce Fault by 23% => 13.25 kApeak
Recovery Under Load
Notes: 18

## Slide 19
Compact MFCL – Fully Tested – 3 seconds

## Slide 20: High Voltage MFCL 138kV at AEP Tidd Substation, Ohio
  Requirements Summary
    Rated 138 kV, 1,300 A
    ~ 20 kA prospective fault
    Reduce fault by 50%
    Recovery under load required
    Fault test single-phase end 2011
    Install 3-phase device mid 2012
FCL
MFCL will replace Air Core Reactors

## Slide 21: 138kV MFCL Design: 3 single-phases

## Slide 22: SUMMARY: Zenergy Power´s MFCL
1st installation of the MFCL in March 2009 at Avanti circuit of Southern California
Edison, utility serving Los Angeles/San Bernardino county, for 1.5 year operation
name plate rating 15 kV / 1,200 A
20% clipping of max. 23 kApeak prospective fault current
Compact MFCL prototype for ConEd in New York City, 2009
rated 13.8 kV / 2,500-4,000 A
successful testing in July 2009, data are confidential to ConEdison
Distribution class MFCL underway for deployment and commissioning in Q3 2011
for ASL/CE Electric in UK
name plate rating 12 kV / 1,250-1,600 A
23% clipping of max. 17 kApeak prospective fault current
2011: ASL ordered 33kV FCL engineering study for CE Electric UK.
Transmission class MFCL in manufacturing for deployment in Mid-2012
for AEP American Electric Power in Ohio
rated 138 kV / 1,300 A
43% clipping of max. 20 kApeak prospective fault current