## Slide 1
The Test and Installation of Medium Class(22.9kV) Hybrid type Fault Current Limiter in KEPCO Grid
Wonjoon Choe
Jungwook Sim
Gyeong-ho Lee
Seung-hyun Bang
Kwon-Bae Park
Young-keun Kim
Ok-Bae Hyun
LS Industrial Systems. Korea
KEPCO/KEPRI. Korea

## Slide 2
SEOUL
ICHEON
HTS hybrid FCL
Cooling System for HTS Cable
Control and Monitoring System
Intermediate connection
of HTS Cable
Offset
Termination
of HTS Cable
170kV GIS
Main Transformer
25.8kV GIS
Application Site : ICHEON 154kV Substation, KEPCO
Installation Location: D/L of M.Tr(154kV/22.9kV) secondary
Real Grid Project of FCL and SC Cable

## Slide 3
Configurations of FCL & SC Cable

## Slide 4
Circuit of Hybrid-type FCL
HTS
Switch Mech.
Reactor
VI
Actuator
Actuator
HTS Backup Switch

## Slide 5
Configurations
Cryocooling System
Switch
Current Limiting Reactor
Cryocooling
Monitoring & Control System

## Slide 6
Specification
Parameter | Specification
Rated Voltage (rms) | 25.8 kV
Rated Current (rms) | 630 A
Rated Power Frequency | 60 Hz
Rated Power Frequency withstand voltage (rms) | 70 kV
Rated Impulse withstand voltage | 150 kV. BIL
Rated short circuit current (rms) | 12.5 kA/1.0 sec
Insulation type | Air
Minimum Limiting Current (rms) | 1.4 kA
Current Limiting Reactor | 0.4 [Ω]
Recovery time | < 0.5 sec
Critical Current of HTS | > 2,000 A
Cooling Power | 220W at 80K
Operation temperature | 75~77K

## Slide 7
HTS wire(CC)
Winding
Stacking
Critical Current
Assembly
Fabrication of HTS trigger module

## Slide 8
Test of FCL
•Test voltage(rms): 22.9/13.2kV
•Test current(rms): 12.5kA
•Fault duration time: -3 phase: 1.0 sec

## Slide 9
Type1
Type2
Non-limited region
Limiting types of fault current limiters

## Slide 10
Protective Coordination in DL
OCR2
OCR1
1
154kV
22.9kV
154/22.9kV
M.Tr
FCL

## Slide 11
Future Plan
• Commercial operation of 25.8kV/630A HTS hybrid FCL 2011.6~ (Planned)
• Development of Fault Current Limiter for Biz. Model ~2011.12(Planned)
  Biz. Model 1: 25.8kV/600A FCL
    - Application site: KEPCO DL (Underground grid)
  Biz. Model 2: 22kV/5,000A FCL
    - Application site : POSCO (Steel plant in Korea)