## Slide 1
Martin J. Lindinger
Herwig Renner
Ernst Schmautzer
Graz University of Technology
Austria
www.ifea.tugraz.at
New Optimized Analysis Method For Measuring Extended Grounding Systems

## Slide 2: Agenda
Problems at grounding measurements
Standard methods
New optimized method
  Principle
  Example
  Results
Conclusion

## Slide 3: Problems at grounding measurements
Low measurement voltages
Low grounding resistance (~mΩ)
Long measurement conductors (~km)
High electromagnetic disturbances

## Slide 4: Fall-of-Potential method

## Slide 5: Signal detection techniques
On/Off-Method
Tuned Voltmeter
Lock-in Amplifier
…
Beat-Frequency-Method
Fourier Transform
New Optimized Method

## Slide 6: Beat-Frequency-Method
Advantages
    Nearly system frequency
    Use of multimeters
    High currents
Disadvantages
    Only compensation of
    system frequency
    Not always clear results

## Slide 7: Fourier Transform
Advantages
    Accurate
    Good filtering of disturbances
Disadvantages
    Electronic power amplifier needed
    No measurements at system frequency
    Low measurement currents
    Expensive measurement equipment

## Slide 8: New Optimized Method (general)
Combination of
    Beat-Frequency-Method
    Fourier Transform
High currents
Nearly system frequency
Standard voltmeters for measuring touch voltages

## Slide 9: New Optimized Method (principle)
Local maxima
Beat-frequencies maxima
T…cycling length of beat signal
Beat signal
Notes: Minimizing leakage effect
Both frequencies of the beat signal are n times in a beat cycle (mathematical exact)

## Slide 10: New Optimized Method (structure)
Digitalization
Beat-cycle length detection
Fourier Transform

## Slide 11: New Optimized Method (structure)
Digitalization
Beat-cycle length detection
Fourier Transform
1st digital filter
Local maxima
2nd digital filter
Beat-signal maxima

## Slide 12: New Optimized Method (example I)
Component at measurement frequency
blue: with peak detection
(3 beat cycles – 1.78s)
red: without peak detection (2s)
Railway system: 16.7 Hz + harmonics
Power system: 50 Hz + harmonics
Measurement signal: 51.69 Hz
Notes: Blau: mit detection (3 beat cycles – 1,78s)
Rot: ohne detection (2s)

## Slide 13: New Optimized Method (example II)
Component at measurement frequency

## Slide 14: New Optimized Method (conclusion)
Advantages
    Nearly system frequency
    High currents
    No disturbances (independent from their frequency)
    Standard voltmeters for measuring touch voltages
Disadvantes
    Digital logger
    Extensive filtering and calculation