## Slide 1: Decentralised Controller for Flicker Mitigation in Converter-Connected DG Networks
Piyadanai Pachanapan, Adam Dysko,
Olimpo Anaya-Lara, Graeme Burt, Kwok L. Lo
Institute for Energy and Environment
University of Strathclyde, Glasgow, UK
21st CIRED, 7th June 2011
RIF Session 2 – Paper ID 1139

## Slide 2: Introduction
New Grid Codes require DG to export reactive power (Q) into MV networks
V/Q support from DG Local Voltage Control
Can Voltage Source Converter (VSC) interfaced DG provide dynamic voltage compensation similar to a STATCOM?
Piyadanai Pachanapan– UK – RIF Session 2 – Paper ID 1139

## Slide 3: Objectives
Use converter-connected DG as decentralised voltage controller to mitigate voltage flicker in MV networks
Reduce the requirements for the deployment of new reactive power compensation devices such as STATCOMs and SVCs.
Piyadanai Pachanapan– UK – RIF Session 2 – Paper ID 1139

## Slide 4
Decentralised Control Structure of a DG network
P-V control scheme of grid-side interfaced VSC

## Slide 5: Voltage flicker mitigation
IEC 61000-3-7
Normalised flickermeter response (Pst = 1.0)

## Slide 6: Test System
Bus 11: 1 MW fixed speed wind turbine
Bus 7: 1 MW p.f. ±0.95(ΔQ = ±0.33 Mvar)
Determine controllable area using voltage sensitivity to Q support from bus 07
Q-V curve is plotted to consider the possible value of V/Q support
Bus voltages inside the zone can receive voltage compensation from DG sufficiently
#1
#2

## Slide 7: Controllable Zone
Guarantee V compensation 0.5-0.7 %
Bus 11: 1 MW fixed speed wind turbine
Bus 7: 1 MW p.f. ±0.95(ΔQ = ±0.33 Mvar)
#1
#2

## Slide 8: Case Study
Flicker is assumed as “Sinusoidal” at bus 11
(ΔV ≈ ±1.0 %, 2 Hz)
Case 1: using converter-connected DG to control the flicker at a remote bus (bus 11)
Case 2: using converter-connected DG to control the flicker at a local bus (bus 7)
Case 3: using only a STATCOM (0.3 MVar) at the flicker source bus 11
Piyadanai Pachanapan– UK – RIF Session 2 – Paper ID 1139

## Slide 9
2 kHz Sinusoidal flicker  ΔV/V < 0.8 % (IEC 61000-3-7)
(Flicker Source)
(VSC-DG Bus)

## Slide 10: Calculate Short term Flicker Index (Pst)
IEC 61000-4-15
(via MATLAB)
Flicker meter
Simulator
Pst
X
AC Sinusoidal
Waveform
RMS flicker
input
10 Minutes
Pst < 1
IEC 61000-3-7
Bus | Pst |  |  | 
 | No compensation | case 1 (remote) | case 2 (local) | case 3 (STATCOM)
6 | 0.3466 | 0.1656 | 0.0709 | 0.0771
7 | 0.6116 | 0.2594 | 0.1659 | 0.1707
11 | 1.0325 | 0.4516 | 0.5870 | 0.3640
17 | 1.0325 | 0.4516 | 0.5870 | 0.3640
24 | 0.0836 | 0.0372 | 0.0383 | 0.0385
25 | 0.3156 | 0.1291 | 0.1145 | 0.1159

## Slide 11: Discussion
Using STATCOM at flicker source bus provides the best flicker mitigation.
Using remote measurement (flicker source) gives better mitigation than using only local measurement (PCC bus of DG), but need communication link.
If voltage sensitivity inside the zone is high, using only local bus control of DG may be sufficient.
Piyadanai Pachanapan– UK – RIF Session 2 – Paper ID 1139

## Slide 12: Conclusions
Converter-connected DG with voltage control ability can mitigate voltage flicker with similar results as using a STATCOM.
Flicker mitigation using converter-connected DG is very effective without communication system requirements, when it is connected near the flicker source.
Piyadanai Pachanapan– UK – RIF Session 2 – Paper ID 1139